# POST REMEDIATION INDOOR AIR QUALITY SAMPLING

Robinson Hall Rowan University Glassboro, NJ 08028

PREPARED FOR:

Rowan University 201 Mullica Hill Road

Glassboro, New Jersey 08028

PREPARED BY:

Montrose Environmental, Inc. 500 Horizon Drive, Suite 540

Robbinsville, NJ 08691

MONTROSE PROJECT NO. 1200-62

### September 2023

TABLE OF CONTENTS

  - INTRODUCTION	1

  - PROJECT OBJECTIVE	1

- METHODOLOGY	2

- MOLD STANDARDS	3

- MOLD ASSESSMENT AND MOISTURE INPSECTION ACTIVITIES	4

  - VISUAL OBSERVATIONS	4

  - ANALYTICAL SAMPLING AND RESULTS	4

  - IDENTIFIED MOLD SPECIES	5

- CONCLUSIONS AND RECOMMENDATIONS	7

APPENDIX A

LABORATORY ANALYTICAL REPORTS

i

# INTRODUCTION

On September 5, 2023 Montrose Environmental, Inc. (Montrose) responded to a request by Rowan University (Rowan) to perform post-remediation indoor air quality (IAQ) sampling throughout Robinson Hall on the Rowan Main Campus in Glassboro, New Jersey (Site). The sampling was requested to assess the efficacy of cleaning efforts done within Robinson Hall that addressed mold growth from recent humidity issues within the building, and visible growth on furniture within the Site.

The building is shut down temporarily to allow for disposal of contaminated furniture, and to allow a fine cleaning of all remaining surfaces. Montrose conducted baseline sampling on August 23, 2023, prior to any furniture removal and cleaning efforts, and again on August 29, 2023, after all furniture had been removed and air scrubbers installed, but before fine cleaning of the interior spaces.

The August 23, 2023 sampling established a baseline of highly elevated mold throughout Robinson Hall, with the August 29, 2023 sampling showing reduction of airborne mold by a significant amount. The September 5, 2023 sampling was done to assess if the mold proliferation within Robinson Hall was resolved, and allow the building to be re-opened, if laboratory results showed significant reductions in airborne mold content and types.

## PROJECT OBJECTIVE

The objective of this project was to collect mold spore air samples and provide recommendations as warranted, based on the laboratory analytical report.

# METHODOLOGY

The air samples were collected utilizing Air-O-Cell sampling cassettes, which are designed for collection and analysis of a wide range of airborne aerosols, including mold spores, pollen, insect parts, fibers, and other inorganic particulates.

All samples were hand delivered to EMSL Analytical, Inc. (EMSL), of Cinnaminson, New Jersey, an American Industrial Hygiene Association Environmental Microbiological Laboratory Accreditation Program (AIHA EMLAP #100194) and Industrial Hygiene Laboratory Accreditation Program (IHLAP) laboratory. All samples were submitted for a 24-hour turnaround time.

# MOLD STANDARDS

Mold growth is most likely found in areas that have sufficient moisture, temperature, and nutritive sources to promote proliferation. Nutritive sources within buildings include drywall paper backing, cellulose ceiling tiles, wallpaper, wood wall framing and trim, pipe insulation wrappings, and similar materials.

As an industry guideline, interpretation of results should be based on comparison of fungi collected from indoor air and outdoor air. Outdoor results are highly variable and can vary based on seasonal conditions and the time-of-day. Additionally, the species of fungi identified in samples collected indoors may vary from those species identified in outdoor samples. Indoor results should be comparable to the types and concentration of fungi outdoors. In some instances, indoor air concentrations of total airborne culturable fungi can exceed outdoor air concentrations, in response to outdoor environmental conditions. The presence of certain indoor-associated species may be indicative of elevated moisture and/or water-damaged building materials. Moreover, the second- edition of the American Industrial Hygiene Association (AIHA) Field Guide for the Determination of Biological Contaminants in Environmental Samples, states that dominance in indoor-air samples by species of molds that are not predominant outdoor species, indicates that molds are growing in the building and that indoor air quality is degraded.

Montrose evaluated the mold spore results using the AIHA Recognition, Evaluation, and Control of Indoor Mold, 2008. Additionally, variability in sampling conditions is considered during the interpretation of laboratory analytical data.

# MOLD ASSESSMENT AND MOISTURE INPSECTION ACTIVITIES

## VISUAL OBSERVATIONS

On September 5, 2023, visible mold growth was no longer observed within most rooms and furniture and surfaces throughout the Site. The only room that had materials with suspect visible mold growth was Room 205, which had cardboard boxes that had not been discarded. A photo is shown below:

Photo 1. Room 205 Cardboard Boxes

All chairs had been removed, and all horizontal flat surfaces wiped down by All Risk.

## ANALYTICAL SAMPLING AND RESULTS

On September 5, 2023, Montrose collected a total of thirty Air-O-Cell samples at the Site. Samples were collected throughout the Site, with approximately ten collected per floor, as directed by the Rowan representative. One additional sample was collected outside the building, for baseline purposes and to determine outdoor background levels of spore concentrations.

The laboratory data indicates that the indoor air is mostly consistent with outdoor air counts. Only three rooms still had slightly elevated counts of Aspergillus/Penicillium, Room 201A, Room 205, and Room 103, with 2,440 spores per cubic meter (s/m3), 1,400 s/m3, and 900 s/m3 respectively, compared to 270 s/m3 outdoors. Several other rooms were in slight exceedance of the outdoor counts for Aspergillus/Penicillium, but not of a significant amount or a level of concern.

Overall counts within the building were significantly reduced from previously observed levels, with all rooms, including those noted above, significantly below the overall outdoor count of 10,284 s/m3. Cleaning efforts throughout the building have reduced the overall mold spore levels down drastically. Air sample laboratory analytical reports have been included in Appendix A.

## IDENTIFIED MOLD SPECIES

The spore types detailed below were analytically determined to be airborne in the samples collected within the Site:

Alternaria is one of the most common fungi worldwide. Its colonies are general found in soil, dead organic debris, on food stuffs, textiles, and weakened plants with discolored leaves. Airborne spores are usually indicative of a humid environment when found indoors, but in most instances, spores found indoors originated from outdoor sources.

Ascospores are discharged during periods of high humidity or rain and are commonly found growing indoors on wet or damp substrates.

Aspergillus/Penicillium is commonly found in soil, plants, and rotting materials. Elevated concentrations are often indicative of water-damaged building materials. It can also be found in the dust at home, carpeting, heating and air conditioning ducts. This fungus commonly settles in human lungs and sinuses.

Basidiospores are released during periods of high humidity or rain and are commonly found in gardens or wooded areas. Mold growth associated with Basidiospores contribute to the destruction of structural building lumber. This spore is a common allergen and may contribute to symptoms associated with hay fever and asthma, and further contribute to symptoms associated with hypersentivity pneumonitis.

Bipolaris/Drechslera is often found in soil, plant debris, and as a plant pathogen on grass with a dark grey to brown coloration, and is found worldwide. For indoor growth this fungus can grow on water damaged materials, food stuffs, houseplants, and other organic materials. These molds are highly common in both indoor and outdoor environments, and most people have some level of exposure on a daily basis. May cause or exacerbate asthma, conjunctivitis, rhinitis, anaphylaxis, angioedema, hives, or pneumonitis and sinusitis in sensitive individuals.

Blakeslea/Choanephora comprise a very small proportion of the fungal biota and may be common in the southeastern areas of the United States. Natural habitat includes soil and plants in tropical and semitropical regions.

Cercospora is often found in plants as a parasite. It is a fungus that causes purple, brown, or black spots on a variety of garden vegetables and shrubs, and is not commonly found indoors, unless interior plants are present.

Cladosporium is commonly found in soil, plants, and decaying plant materials. Concentrations may be found on many different substrates, including but not limited to: textiles, wood, and window sills. Cladosporium is a common allergen and may contribute to symptoms associated with hay fever and asthma, and further contribute to symptoms associated with hypersensitivity pneumonitis.

Curvularia is often found in plant debris, soil, facultative plant pathogens or tropical plants with a gray or brown coloration. Curvularia is a relatively common cause of allergic fungal sinusitis,

specifically within immunocompromised individuals.

Epicoccum is commonly found on a variety of household materials, including wood, drywall, fabric, carpet, mattresses and painted surfaces. This species is commonly found in plant debris and soil. Presence of this mold can trigger allergic reactions and can also cause respiratory problems.

Ganoderma is often found growing on conifers and hardwoods causing white rot, root rot, and stem rot, and is considered to be an allergen. Not often found indoors, and only usually present on rotting wood surfaces.

Myxomycetes is found usually in decaying logs, stumps, and dead leaves, particularly in forested regions. Occasionally found indoors on damp building materials such as cardboard, wallpaper, gypsum and wood, it is considered a slime-mold, and can be found world-wide. In sensitive individuals, allergic reactions may occur, including asthma, conjunctivitis, rhinitis, dermal swelling and hives.

Oidium species, or ‘powdery mildew,’ are obligate plant pathogens, as they are completely dependent on living hosts. They cannot be cultivated in a laboratory, separate from their hosts. Affecting only flowering plants, powdery mildew can be found on various trees, grapes, beans, cereal crops, crucifers, cucurbits, roses, various trees, and weeds. It is estimated that about 10,000 plant species are susceptible to powdery mildew, making powdery mildew one of the most widespread plant diseases.

Pithomyces is often found in dead leaves, especially leaf fodders as well as in soil and grasses with a tan to brown coloration. It is rarely found indoors unless growing on paper or houseplants.

Polythrincium is often found in dead leaves and is rarely found indoors. Spores may be seen in dust as part of the normal influx of outdoor microbial particles to indoor environments.

Rust is often found in grasses, flowers, trees, and other living plant materials. For growth this fungus requires a living host plant for growth, so it is not found on interior building components. As an allergen, it has been known to cause hay fever and asthma.

To date, there are no threshold limits or recommendations for levels of indoor mold aeroallergens. The Occupational Safety and Health Administration (OSHA), the National Institute of Occupational Safety and Health (NIOSH), as well as other occupational health related associations, have not established permissible exposure levels (PELs), recommended exposure limits (RELs), or other compliance limit values for aeroallergens. In general, spore counts and spore types are influenced by geographic location, seasonal and diurnal cycles, as well as outdoor conditions. Therefore, it is difficult for regulatory agencies and industry groups to establish permissible exposure limits for mold and fungi exposure, and as a result, there are no regulatory quantitative exposure limits for airborne mold or fungi.

# CONCLUSIONS AND RECOMMENDATIONS

Based on the September 5, 2023, visual inspection and sampling, All Risk has successfully cleaned Robinson Hall, with exception to Room 201A, 205, and 103. Aspergillus/Penicillium counts within those rooms is still elevated, and those rooms should be re-cleaned. The cardboard boxes observed within Room 205 should be discarded as well.

For the rooms noted above, all horizontal surfaces, including flooring, throughout building should be wet-wiped and vacuumed with a High Efficiency Particulate Air (HEPA) filter, to collect any spores that may have settled, and an air scrubber installed to filter any airborne particulates.

Once cleaning has been completed by AllRisk, Montrose recommends that Rowan perform air testing within those three rooms, to assess the efficacy of all cleaning and disposal activities, prior to those rooms being re-occupied. The remainder of Robinson Hall may be occupied, presuming the three rooms noted above are isolated until satisfactory cleaning has been conducted.

### -o.0.o-

These results represent the conditions and concentrations present at the time of this survey. Respectfully Submitted,

MONTROSE ENVIRONMENTAL, INC.

Jessica Perrini	Julian Fernandez-Obregon

Project Health & Safety Specialist	Director, Health & Safety Division

APPENDIX A

Laboratory Analytical Reports

♦

OrderID: 372313960

EMSL ANALYTICAL., INC.

Tl.STING	• "911:0DUCTS • TIIAJMNG

Microbiology Chain of Custody Form

EMSL Orde Number/ Lab Use Only

37d-3/3

0

c,111.:,L lalyUGi:11, IIIG.

200 Roule 130 North

Cinnaminson, NJ 08077

PHONE: (800) 220-3675

EMAIL: CinnMlcroLab@emsl.com

r81 To is the..,,,. u Raoo,t-To "'-  l!llo section blanl<. Thi'll'lllrt)'	nquirN wrtl8n out/loriz.allo<>.

Customer ID:	BilllrQ ID:

i5 CompanyName: /Y) fj /'J f ( 6 S e,_ Yh I }I '('/)yyJ /J Y1H"'  f

Company Name:

I\ 	n 	b

k------''-L-4-Jl,L.(....LL-.:...,,:c....e:::	  J ...LJ.L.'..-'-"--'LL.Ll..,A....LL....l.<l..._ _  1	t

E ContactName: ,\ t l	(l,\l\,  l( 	.0,1'"\rl<.-z.. -(')	r-e.C(	i Billing Contact:

i.. Street Address: m') Hort'? .._ 	i\,. Su.,...,_, s-t/ 0-.J	I	j Street Address:

C:1	I

| City, State, Zip h h,"- c 1, | Il 1' N 1,--- | ICOUllty: | =-j,_c_ay. · s_la_te_, Zi | ip_: | eou_n_try:_. | --< |
| --- | --- | --- | --- | --- | --- | --- |
| Phone: | (/ |  | Phon:e |  |  |  |

E

u	1--Email-(s--,)or-R_eport_\_-C_trf_l'\_U,_Yr) l_t_7_/6Jj'()"C()--\-JO-)-\e_-{_11  J_(i-Ot'-l1--I

Email(s) for Invoice:

Project Name/No:

EMSL LIMS Project ID:

kl/ appbl,lo, EMSL wll

)

Slate Samples Collected:

Prqject Information

Zip Code Samples Collected::

Purchase Order:

D	D

Slate of Connecticut (CT) must select project location: Commercial (Taxable)	Residential {Non-taxable)

Sampled By Name:	Sampled By SignalurEM

Sterile, Sodium Thlo5ulfate Preserved Bottle Used:0	Blocide Used fn Source (specify)

Public Water Supply Sampl8$:0	Note: All ijo..ults may a.utomatlcally be reported to DOH If required by Stale.

No. o1 Samples

I

n l

D3Hour	D	&Hour

r.11Tum-Around•TI An	-..-.i..g.o ---•mu&tbnott.- "32 ..... TATrnllableto,,.i.:t<estsodf:"""IMS"""'	,.,,,".. by'1:301m,

D	D	D	D1	D

00 24 Hour	LJ 3%" Hour	4-8 Hour	72 Hour	96 Hour	Week	2 Week

MICROBIOLOGY TEST: CODES

M001 Air-0-Cell	M174 Mok!Snap	M012 Pseudomonas aeruglnosa {P/A-•)

1--------------1------------

M0J0 Micro 5	M032 ADergenco-0	M024 Pseudomonas aerugfnosa  FT')

-M0-41-Fu-nga-l D-ire-ct E-xa-min-atio'n ------------M015 Heterotrophic	le Counl

M169 Pollen ID & EnumeraUon	M017 Total Coliform  E. Coll {COfilert P/A-)

M280 Dust CharacterizationLe•el-1	M018 Total Coliform\ E Coli (MFT")

M281 Dust Characterization Level-2	M114 Total CoUfonn & E Coli Enumeration (Colilert MPN-)

M005 Viable Fungi-Air Samples (Gen.is ID & Count)	M019 Fecal Coiform (MFT') MOO&Viable Fungi-Air Samples (Includes Penicfllum, Aspergillus,	 M020 Fecal Streptococcus (MFT")

Cladosporium, Stachybot,ys Species ID & Count)	Mo2g Enterococci {MFT")

M007 CIAll,able Fungi-Surface Samples (Genus ID & Count}	 M129 Enterococci (Enterolert P/A0-) MOOSCulturable Fungi-Surface Samples (Includes Pen/ell/um,	M180 Real rime qf'<f-ERMI 36 Panel

Asperg11/us, Cladosporium, Stachybo/Iys Species 10 & Count)	Mo25 Sewage Scree1_Water(MFT')

M115 Sewage Screen -Water (P/A-)

M116 Sewage Screen - Water (MP .. ) M117 Sewage Screen-Swab -·)

M013 Sewage Screen - Swab <@·> £?

M730 Methicillin-resistant Staph,f)J!8US tisA)

M031 Rapid-<Jrowing non-TB M cter$9e t,

I	-:Irr,

Eluneratlon	3, I ' I ('")

M014 Endoloxin Analysis	U,	ffiCJ> -

M0-44 Group Anergen (Cat, Dog.roa

.	'

M095 Bacteroides	?= 0

Other- See Analytical Price Guide4i'r'Test e

Legionella Analysis Please use ct13- L lls COC

M009 Bacteria Cultlre Gram Stain & Co\.nl M010 Bacteria Co'6ll & ID - 3 Most Prominent M011 Bacteria Count & ID - 5 Most Prominent

"MFT= Membrane Filtration Technique PN	= Most Probable Number

-p/A " Presence/Absence

'VM.	3\\

\	I	I	\

V

Special Instructions arvJ/or Regulatory Requirements (Sample Specifications, Processing Melrods, Limits or Detection, etc.) '--"

Method or Shipment	Sample Condition Upon Receipt

Refr,ql.ished by:

Datetrime:

I

Relinquishedby:

DalelTime:	I

Receiv?bY--

Datenunp'

COnlrolod Docu1N11l - COC-34 Micro R13 03/0V2021

LJ AGREE TO ELECTRONIC SIGNATURE (By cheddng, I consent to signing this Chain of Custody document by electronic slgnalure.)

EMSL Analytical, lnc.'s Laboratory Tenms and Conditions are Incorporated into th/s Chain of Custody by reference in their entirety. Submis51on of sample.s to EMSL Analytical, Inc. constitutes acceptance and acknowledgment of all terms and conditions by Cu5tomer.

Page 1 Of	2

0-;:1no 1 nf

♦

OrderID: 372313960

L

oiEI\IISL ANALYTICAL, INC.

,..,.1lJTING LA.BS• PRODUCTS• TRAINING

U:::

### Microbiology Chain of Custody Form

EMSL OrdJr Number/ lab Use Only

EMSL Analytical, Inc.

200 Route 130 North

Cinnaminson, NJ 08077

PHONE:(800) 220-3675

EMAIL'.CinnMicroLab@emsl.com

l".;Additbnal P es of the Chain of Cus:tod 8(9 ofll nae	l l't88d8d for additional sam a ilformadon

'.\ r'1 f.	Special Instructions and/or Regulato,y Requirements (Sample Specifications, Processing Methods, Limits of Detection, etc.)

' "•'

Sample#

Sample Location/Description

Sample Type (Matrix)

Pptable /	Non- Potable (Only for Water)

Test Code

Volume/Area

Date/ Time Collected

Temperature (Lab Use Only)

JO 3

Sample Condition Upon Receipt:

Relinqu,

Con-troned Document • COC..J4 Micro R13 3102/2021

I. -

[

DateTTimeq  /S

□

DatefTime:

AGREE TO ELECTRONIC SIGNATURE (By checking, I consenl to signing this Chain of Custody documenl by electronic signature.)

Incorporated nto this Cha

n of Custody

\ . .	EMSL Analytical, lnc.'s Laboratory Tenns and Conditions are Page 2 Of	i 2

by referenc•e In their entirety. Submission of samples to EMSL

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0001 RRU-01 150 |  |  | 372313960-0002 RRU-02 150 |  |  | 372313960-0003 RRU-03 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 305 |  |  | RM 311 |  |  | RM 306 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 25 | 550 | 28.1 | - | - | - | 12 | 260 | 86.7 |
| Basidiospores | 14 | 310 | 15.8 | 4 | 90 | 56.3 | 1 | 20 | 6.7 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 50 | 1100 | 56.1 | 3 | 70 | 43.8 | 1 | 20 | 6.7 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 89 | 1960 | 100 | 7 | 160 | 100 | 14 | 300 | 100 |
| Hyphal Fragment | 2 | 40 | - | - | - | - | 1 | 20 | - |
| Insect Fragment | 1 | 20 | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 1 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 1 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0004 RRU-04 150 |  |  | 372313960-0005 RRU-05 150 |  |  | 372313960-0006 RRU-06 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 302 |  |  | RM 306A |  |  | RM 303 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | - | - | - | 17 | 370 | 81 | - | - | - |
| Basidiospores | - | - | - | 2 | 40 | 8.8 | 10 | 220 | 71 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 1 | 20 | 4.4 | 4 | 90 | 29 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | 1* | 7* | 1.5 | - | - | - |
| Pithomyces++ | - | - | - | 1 | 20 | 4.4 | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | - | None Detect | - | 22 | 457 | 100 | 14 | 310 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 2 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 2 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0007 RRU-07 150 |  |  | 372313960-0008 RRU-08 150 |  |  | 372313960-0009 RRU-09 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RMG1 |  |  | RM 304 |  |  | Hallway RM 323 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 2 | 40 | 11.8 | - | - | - | - | - | - |
| Basidiospores | 9 | 200 | 58.8 | - | - | - | 1 | 20 | 29.9 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 6 | 100 | 29.4 | 1 | 20 | 100 | 2 | 40 | 59.7 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | 1* | 7* | 10.4 |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 17 | 340 | 100 | 1 | 20 | 100 | 4 | 67 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 1 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 3 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0010 RRU-10 150 |  |  | 372313960-0011 RRU-11 150 |  |  | 372313960-0012 RRU-12 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hallway RM 311 |  |  | RM 207 |  |  | RM 201A |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | 1 | 20 | 5.4 | - | - | - |
| Aspergillus/Penicillium | - | - | - | 7 | 200 | 54.5 | 112 | 2440 | 94.9 |
| Basidiospores | 2 | 40 | 100 | 2 | 40 | 10.9 | 3 | 70 | 2.7 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 5 | 100 | 27.2 | 2 | 40 | 1.6 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | 1 | 20 | 0.8 |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | 1* | 7* | 1.9 | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 2 | 40 | 100 | 16 | 367 | 100 | 118 | 2570 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 2 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 4 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0013 RRU-13 150 |  |  | 372313960-0014 RRU-14 150 |  |  | 372313960-0015 RRU-15 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 202 |  |  | Hallway RM 213 & 214 |  |  | RM 230 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 13 | 280 | 87.5 | 2 | 40 | 40 | - | - | - |
| Basidiospores | 2 | 40 | 12.5 | 2 | 40 | 40 | - | - | - |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 1 | 20 | 20 | - | - | - |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 15 | 320 | 100 | 5 | 100 | 100 | - | None Detect | - |
| Hyphal Fragment | - | - | - | 1 | 20 | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | 1 | 20 | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 2 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 5 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0016 RRU-16 150 |  |  | 372313960-0017 RRU-17 150 |  |  | 372313960-0018 RRU-18 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 206 |  |  | RM 205 |  |  | RM 201B |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 3 | 70 | 6.1 | 66 | 1400 | 95.2 | 7 | 200 | 100 |
| Basidiospores | 7 | 200 | 17.5 | 3 | 70 | 4.8 | - | - | - |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 40 | 870 | 76.3 | - | - | - | - | - | - |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 50 | 1140 | 100 | 69 | 1470 | 100 | 7 | 200 | 100 |
| Hyphal Fragment | 4 | 90 | - | 1 | 20 | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 22 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 2 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 6 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0019 RRU-19 150 |  |  | 372313960-0020 RRU-20 150 |  |  | 372313960-0021 RRU-21 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 204 |  |  | Hallway 216 & 206 |  |  | RM 100 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 8 | 200 | 64.5 | - | - | - | 14 | 290 | 82.9 |
| Basidiospores | 1 | 20 | 6.5 | - | - | - | 2 | 40 | 11.4 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 4 | 90 | 29 | 1 | 20 | 100 | 1 | 20 | 5.7 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 13 | 310 | 100 | 1 | 20 | 100 | 17 | 350 | 100 |
| Hyphal Fragment | 1* | 7* | - | 1 | 20 | - | 3 | 60 | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 22 | - | - | 22 | - | - | 21 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 1 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 7 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0022 RRU-22 150 |  |  | 372313960-0023 RRU-23 150 |  |  | 372313960-0024 RRU-24 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 101A |  |  | RM 105 |  |  | RM 102 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 3 | 60 | 37.5 | 5 | 100 | 19.2 | 15 | 310 | 82.2 |
| Basidiospores | 2 | 40 | 25 | 9 | 200 | 38.5 | 2 | 40 | 10.6 |
| Bipolaris++ | - | - | - | - | - | - | 1* | 7* | 1.9 |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 3 | 60 | 37.5 | 9 | 200 | 38.5 | 1 | 20 | 5.3 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | 1 | 20 | 3.8 | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 8 | 160 | 100 | 24 | 520 | 100 | 19 | 377 | 100 |
| Hyphal Fragment | - | - | - | 5 | 100 | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 21 | - | - | 21 | - | - | 21 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 1 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 8 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0025 RRU-25 150 |  |  | 372313960-0026 RRU-26 150 |  |  | 372313960-0027 RRU-27 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 115 |  |  | RM 103 |  |  | RM 101B |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | 1 | 20 | 0.9 | - | - | - |
| Aspergillus/Penicillium | 3 | 60 | 50 | 44 | 900 | 38.5 | 28 | 570 | 58.8 |
| Basidiospores | 2 | 40 | 33.3 | 14 | 290 | 12.4 | 9 | 200 | 20.6 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 1 | 20 | 16.7 | 53 | 1100 | 47.1 | 9 | 200 | 20.6 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | 1 | 20 | 0.9 | - | - | - |
| Rust | - | - | - | 1* | 7* | 0.3 | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Blakeslea/Choanephora | - | - | - | - | - | - | - | - | - |
| Botrytis | - | - | - | - | - | - | - | - | - |
| Cercospora++ | - | - | - | - | - | - | - | - | - |
| Oidium++ | - | - | - | - | - | - | - | - | - |
| Pestalotia++ | - | - | - | - | - | - | - | - | - |
| Polythrincium | - | - | - | - | - | - | - | - | - |
| Total Fungi | 6 | 120 | 100 | 114 | 2337 | 100 | 46 | 970 | 100 |
| Hyphal Fragment | 1 | 20 | - | 4 | 80 | - | 2 | 40 | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | 1* | 7* | - |
| Analyt. Sensitivity 600x | - | 21 | - | - | 21 | - | - | 21 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 2 | - | - | 2 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 9 of 10

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313960-0028 RRU-28 150 |  |  | 372313960-0029 RRU-29 150 |  |  | 372313960-0030 RRU-30 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hallway RM 118 |  |  | Hallway RM 101A |  |  | Outside |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | 6 | 100 | 1 |
| Ascospores | - | - | - | - | - | - | 64 | 1300 | 12.6 |
| Aspergillus/Penicillium | 3 | 60 | 56.1 | 1 | 20 | 10 | 13 | 270 | 2.6 |
| Basidiospores | - | - | - | 4 | 80 | 40 | 112 | 2300 | 22.4 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 1 | 20 | 18.7 | 6 | 100 | 50 | 264 | 5420 | 52.7 |
| Curvularia | 1* | 7* | 6.5 | - | - | - | 3 | 60 | 0.6 |
| Epicoccum | - | - | - | - | - | - | 1 | 20 | 0.2 |
| Ganoderma | - | - | - | - | - | - | 16 | 330 | 3.2 |
| Myxomycetes++ | - | - | - | - | - | - | 5 | 100 | 1 |
| Pithomyces++ | - | - | - | - | - | - | 1* | 7* | 0.1 |
| Rust | - | - | - | - | - | - | 5 | 100 | 1 |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | 1 | 20 | 18.7 | - | - | - | 6 | 100 | 1 |
| Blakeslea/Choanephora | - | - | - | - | - | - | 3* | 20* | 0.2 |
| Botrytis | - | - | - | - | - | - | 1 | 20 | 0.2 |
| Cercospora++ | - | - | - | - | - | - | 5 | 100 | 1 |
| Oidium++ | - | - | - | - | - | - | 2* | 10* | 0.1 |
| Pestalotia++ | - | - | - | - | - | - | 1* | 7* | 0.1 |
| Polythrincium | - | - | - | - | - | - | 1 | 20 | 0.2 |
| Total Fungi | 6 | 107 | 100 | 11 | 200 | 100 | 509 | 10284 | 100 |
| Hyphal Fragment | 3 | 60 | - | 4 | 80 | - | 41 | 840 | - |
| Insect Fragment | - | - | - | - | - | - | 2 | 40 | - |
| Pollen | - | - | - | - | - | - | 5 | 100 | - |
| Analyt. Sensitivity 600x | - | 21 | - | - | 21 | - | - | 21 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 2 | - | - | 2 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 2 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

Skin Fragment and Fibrous Particulate ratings are based on the percent of non-fungal material they represent: 1 (1-25%), 2 (26-50%), 3 (51-75%), or 4 (76-100%). Background ratings are based on the total area covered by non-fungal particles: 1 (1-25%), 2 (26-50%), 3 (51-75%), 4 (76-99%), or 5 (100%; overloaded, prohibiting accurate detection and quantification). High levels of background will obscure spores and other particulates, leading to underestimation. Present = Spores detected on overloaded samples. Results are not blank corrected unless otherwise noted. The detection limit is equal to one fungal spore, structure, pollen, fiber particle or insect fragment. "*" Denotes particles found at 300X. "-" Denotes not detected. Due to method stopping rules, raw counts in excess of 100 are extrapolated based on the percentage analyzed. EMSL maintains liability limited to cost of analysis.

Interpretation and use of test results are the responsibility of the client. This report relates only to the samples reported above, and may not be reproduced, except in full, without written approval by EMSL. EMSL bears no responsibility for sample collection activities or analytical method limitations. The report reflects the samples as received. When the information supplied by the customer can affect the validity of the result, it will be noted on the report.

Samples analyzed by EMSL Analytical, Inc. Cinnaminson, NJ AIHA LAP, LLC-EMLAP Accredited #100194

Initial report from: 09/06/2023 03:57 PM

For information on the fungi listed in this report, please visit the Resources section at www.emsl.com

MIC_M001_0002_0002 Printed: 09/06/2023 03:57 PM	Page 10 of 10