# ADDITIONAL INDOOR AIR QUALITY SAMPLING

Robinson Hall Rowan University Glassboro, NJ 08028

PREPARED FOR:

Rowan University 201 Mullica Hill Road

Glassboro, New Jersey 08028

PREPARED BY:

Montrose Environmental, Inc. 500 Horizon Drive, Suite 540

Robbinsville, NJ 08691

MONTROSE PROJECT NO. 1200-62

### September 2023

TABLE OF CONTENTS

  - INTRODUCTION	1

  - PROJECT OBJECTIVE	1

- METHODOLOGY	2

- MOLD STANDARDS	3

- MOLD ASSESSMENT AND MOISTURE INPSECTION ACTIVITIES	4

  - VISUAL OBSERVATIONS	4

  - ANALYTICAL SAMPLING AND RESULTS	4

  - IDENTIFIED MOLD SPECIES	4

- CONCLUSIONS AND RECOMMENDATIONS	7

APPENDIX A

LABORATORY ANALYTICAL REPORTS

i

# INTRODUCTION

On August 29, 2023 Montrose Environmental, Inc. (Montrose) responded to a request by Rowan University (Rowan) to perform a second round of indoor air quality (IAQ) sampling throughout Robinson Hall on the Rowan Main Campus in Glassboro, New Jersey (Site). The sampling was requested in response to recent humidity issues that have allowed mold to proliferate within the building, and visibly grow on furniture within the Site.

The building is shut down temporarily to allow for disposal of contaminated furniture, and to allow a fine cleaning of all remaining surfaces. The purpose of the previous sampling on August 23 was to establish a baseline for comparison before and after remediation activities have completed. Now that AllRisk has begun decontaminating the rooms Montrose was tasked with a second round of comparative sampling.

## PROJECT OBJECTIVE

The objective of this project was to collect mold spore air samples, mold surface samples, and provide recommendations as warranted, based on the laboratory analytical report.

# METHODOLOGY

The air samples were collected utilizing Air-O-Cell sampling cassettes, which are designed for collection and analysis of a wide range of airborne aerosols, including mold spores, pollen, insect parts, fibers, and other inorganic particulates.

All samples were hand delivered to EMSL Analytical, Inc. (EMSL), of Cinnaminson, New Jersey, an American Industrial Hygiene Association Environmental Microbiological Laboratory Accreditation Program (AIHA EMLAP #100194) and Industrial Hygiene Laboratory Accreditation Program (IHLAP) laboratory. All samples were submitted for a 24-hour turnaround time.

# MOLD STANDARDS

Mold growth is most likely found in areas that have sufficient moisture, temperature, and nutritive sources to promote proliferation. Nutritive sources within buildings include drywall paper backing, cellulose ceiling tiles, wallpaper, wood wall framing and trim, pipe insulation wrappings, and similar materials.

As an industry guideline, interpretation of results should be based on comparison of fungi collected from indoor air and outdoor air. Outdoor results are highly variable and can vary based on seasonal conditions and the time-of-day. Additionally, the species of fungi identified in samples collected indoors may vary from those species identified in outdoor samples. Indoor results should be comparable to the types and concentration of fungi outdoors. In some instances, indoor air concentrations of total airborne culturable fungi can exceed outdoor air concentrations, in response to outdoor environmental conditions. The presence of certain indoor-associated species may be indicative of elevated moisture and/or water-damaged building materials. Moreover, the second- edition of the American Industrial Hygiene Association (AIHA) Field Guide for the Determination of Biological Contaminants in Environmental Samples, states that dominance in indoor-air samples by species of molds that are not predominant outdoor species, indicates that molds are growing in the building and that indoor air quality is degraded.

Montrose evaluated the mold spore results using the AIHA Recognition, Evaluation, and Control of Indoor Mold, 2008. Additionally, variability in sampling conditions is considered during the interpretation of laboratory analytical data.

# MOLD ASSESSMENT AND MOISTURE INPSECTION ACTIVITIES

## VISUAL OBSERVATIONS

On August 29, 2023, visible suspect mold growth was observed on furniture and surfaces throughout the Site, with representative photos below:

Photo 1. Containment and Dehumidifier	Photo 2. Possible Mold Stains

Approximately 750 chairs were distributed across all three floors, and all were removed. All Risk has begun constructing containments, and using dehumidifiers in each room to mitigate humid conditions as depicted in Photo 1. Suspect visible mold growth was still identified on several tables and horizontal surfaces throughout the Site, such as the above depicted in Photo 2. The fine cleaning was scheduled to begin the next day.

## ANALYTICAL SAMPLING AND RESULTS

On August 29, 2023, Montrose collected a total of thirty Air-O-Cell samples at the Site. Samples were collected throughout the Site, with approximately ten collected per floor, as directed by the Rowan representative. One additional sample was collected outside the building, for baseline purposes and to determine outdoor background levels of spore concentrations.

The laboratory data indicates that the indoor air still contains elevated counts of Aspergillus/Penicillium of varying amounts throughout the Site, ranging from 20 spores per cubic meter (s/m3) to 8570 s/m3, which is a reduction in the range found from the first sampling. Cladosporium levels were also elevated throughout the Site. Elevated amounts of both species, in exceedance of the outdoor counts of both, are of indicative of proliferating mold within the Site. Air sample laboratory analytical reports have been included in Appendix A.

## IDENTIFIED MOLD SPECIES

The spore types detailed below were analytically determined to be airborne in the samples collected within the Site:

Alternaria is one of the most common fungi worldwide. Its colonies are general found in soil, dead organic debris, on food stuffs, textiles, and weakened plants with discolored leaves. Airborne spores are usually indicative of a humid environment when found indoors, but in most instances, spores found indoors originated from outdoor sources.

Ascospores are discharged during periods of high humidity or rain and are commonly found growing indoors on wet or damp substrates.

Aspergillus/Penicillium is commonly found in soil, plants, and rotting materials. Elevated concentrations are often indicative of water-damaged building materials. It can also be found in the dust at home, carpeting, heating and air conditioning ducts. This fungus commonly settles in human lungs and sinuses.

Basidiospores are released during periods of high humidity or rain and are commonly found in gardens or wooded areas. Mold growth associated with Basidiospores contribute to the destruction of structural building lumber. This spore is a common allergen and may contribute to symptoms associated with hay fever and asthma, and further contribute to symptoms associated with hypersentivity pneumonitis.

Bipolaris/Drechslera is often found in soil, plant debris, and as a plant pathogen on grass with a dark grey to brown coloration, and is found worldwide. For indoor growth this fungus can grow on water damaged materials, food stuffs, houseplants, and other organic materials. These molds are highly common in both indoor and outdoor environments, and most people have some level of exposure on a daily basis. May cause or exacerbate asthma, conjunctivitis, rhinitis, anaphylaxis, angioedema, hives, or pneumonitis and sinusitis in sensitive individuals.

Cercospora is often found in plants as a parasite. It is a fungus that causes purple, brown, or black spots on a variety of garden vegetables and shrubs, and is not commonly found indoors, unless interior plants are present.

Cladosporium is commonly found in soil, plants, and decaying plant materials. Concentrations may be found on many different substrates, including but not limited to: textiles, wood, and window sills. Cladosporium is a common allergen and may contribute to symptoms associated with hay fever and asthma, and further contribute to symptoms associated with hypersensitivity pneumonitis.

Curvularia is often found in plant debris, soil, facultative plant pathogens or tropical plants with a gray or brown coloration. Curvularia is a relatively common cause of allergic fungal sinusitis, specifically within immunocompromised individuals.

Epicoccum is commonly found on a variety of household materials, including wood, drywall, fabric, carpet, mattresses and painted surfaces. This species is commonly found in plant debris and soil. Presence of this mold can trigger allergic reactions and can also cause respiratory problems.

Ganoderma is often found growing on conifers and hardwoods causing white rot, root rot, and stem rot, and is considered to be an allergen. Not often found indoors, and only usually present on rotting wood surfaces.

Myxomycetes is found usually in decaying logs, stumps, and dead leaves, particularly in forested regions. Occasionally found indoors on damp building materials such as cardboard, wallpaper, gypsum and wood, it is considered a slime-mold, and can be found world-wide. In sensitive individuals, allergic reactions may occur, including asthma, conjunctivitis, rhinitis, dermal swelling and hives.

Pithomyces is often found in dead leaves, especially leaf fodders as well as in soil and grasses with a tan to brown coloration. It is rarely found indoors unless growing on paper or houseplants.

Polythrincium is often found in dead leaves and is rarely found indoors. Spores may be seen in dust as part of the normal influx of outdoor microbial particles to indoor environments.

Rust is often found in grasses, flowers, trees, and other living plant materials. For growth this fungus requires a living host plant for growth, so it is not found on interior building components. As an allergen, it has been known to cause hay fever and asthma.

To date, there are no threshold limits or recommendations for levels of indoor mold aeroallergens. The Occupational Safety and Health Administration (OSHA), the National Institute of Occupational Safety and Health (NIOSH), as well as other occupational health related associations, have not established permissible exposure levels (PELs), recommended exposure limits (RELs), or other compliance limit values for aeroallergens. In general, spore counts and spore types are influenced by geographic location, seasonal and diurnal cycles, as well as outdoor conditions. Therefore, it is difficult for regulatory agencies and industry groups to establish permissible exposure limits for mold and fungi exposure, and as a result, there are no regulatory quantitative exposure limits for airborne mold or fungi.

# CONCLUSIONS AND RECOMMENDATIONS

Based on the August 29, 2023, visual inspection and sampling, mold is present and proliferating within Robinson Hall, although the removal of contaminated furniture has reduced the airborne counts slightly overall. As AllRisk is still in the process of removal of furniture, and has yet to perform the cleaning, Montrose’s recommendations for the cleanup still stand:

- All water damaged drywall and ceiling tiles to be immediately removed from the site. Dehumidifiers should be kept in place, if possible, to reduce relative humidity.

- All cardboard boxes, cork boards, crates, coverings, and furniture throughout the affected areas should be discarded, if possible. Spores have likely settled on the existing materials.

  - If disposal is not an option, those items, when possible, should be thoroughly cleaned and removed from the room.

- All partition/dividing walls (non-concrete ones), carpeting and flooring in the affected areas should be cleaned and treated with an antimicrobial coating, such as Microban, or equivalent.

- Any walls that are drywall should be examined for mold damage, and wiped down, if possible (most walls are concrete).

- All horizontal surfaces, including flooring, throughout building should be wet-wiped and vacuumed with a High Efficiency Particulate Air (HEPA) filter, to collect any spores that may have settled.

Once cleaning has been completed by AllRisk, Montrose recommends that Rowan perform clearance air testing, to assess the efficacy of all cleaning and disposal activities, prior to the building being released for general re-occupancy.

### -o.0.o-

These results represent the conditions and concentrations present at the time of this survey. Respectfully Submitted,

MONTROSE ENVIRONMENTAL, INC.

Jessica Perrini	Julian Fernandez-Obregon

Project Health & Safety Specialist	Director, Health & Safety Division

APPENDIX A

Laboratory Analytical Reports

OrderID: 372313541

]fd-J \'JSt.\ \

Microbiology Chain of Custody

EMSL Order Number (Lab Use Only):

PHONE:

Company:

Montrose Enviromental

FAX:

EMSL-B111   to:,b-JDifferentmusame

If BIii to Is Different no e nstnJctlons In Com e s••

Street: 500 Horizon Drive, Suite 540

City: Robbinsville	I State/Province: NJ

Report To (Name): Julian Fernandez-Obregon

Emall Address:	jfemandez@montrose-env.com

Project Name/Number:  Wowtln-	l!ob),..34,, Holl	I;,1.l»--b3

U.S. State Samples Taken:  NJ

Third Party Bil/Ina reQuires written authorization from third party

Zip/Postal Code: 08691	I Country: USA

Telephone #: 609-890-7277

Fax #: 609-890-9116	l Purchase Order:

Please Provide Results: DrAX OClE-mail nMail

Connecticut Samples: D Commercial D Resldentlal

□

Turnaround Time (TAT) Options* - Please Check

U 3 Hour	I  D 6 Hour  I	IX24 Hour	1 148 Hour	I LJ 72 Hour	I 196 Hour	I	1 Week	I	I 12 Week

- Analysis completed in accordance with EMSL's Terms and Conditions located in the Analytical Price Gulde. TATs are subject to methodoioav requirements

Non  Culturable Air Samples (Spore Traps) - Test Codes

| - M001 Air-O-Cell | - M173 Allegro M2 | - M004 Allergenco | - M032 Allergenco-D | - M172 Versa Trap |
| --- | --- | --- | --- | --- |
| - M049 BioSIS - M030 Micro 5 | - M003 Burkard - M174 MoldSnao | - M043 Cyclex - M176 Relle Smart | - M002 Cyclex-d - M130 Via-Cell |  |

Other Mlcrobloloav 1:est Codes

- M041 Fungal Direct Examination	•	M014 Endotoxin Analysis	•	M029 Enleroc:occi

- MOOS Viable Fungi ID and Count	•	M015 Heterotrophic Plate Count	•	M019 J='ecal Coliform

- M006 Viable Fungi ID and Count (Speciation)	•	M180 Real Time Q-PCR-ERMI 36	•	M133 MRSA AgalysT

- M007 Culturable Fungi	•	Panel	•	M028toCf!!!_ffltieoformans

- MOOS Culturable Fungi (Speciation)	•	M018 Total Coliform	Detecti	_ :r,

- M009 Gram Stain Culturable Bacteria	(Membrane Filtration)	•	M120 ,stopla sulatum

- M010 Bacterial Count and ID - 3 Most	•	M020 Fecal Streptococcus	Detecti	'.l	1

Prominent	(Membrane Filtration}	•	M033-39  llergen Testing

- M011 Bacterial Count and ID - 5 Most	•	M210-215 Legionella Detection	•	M044 Gl'OUp Allergen	1

Prominent

- M013 Sewage Contamination in Buildings

Preservation Method (Water):

- M026 Recreational Water Screen

- M027 Mycotoxin Analysis

(Cat, DQQICocKroach, Dustmites)

- Other Sa>Analytical Price GuidE-

Name of Sampler:

C(} II/ Or/aifllt

Signature of Sampler:  "2		-

Sample#

Ex, mple: A1

Sample Location

Kitchen

Sample Type

Air

Test Code

M001

Volume/Area

75L

DatefTlme Collected

1/1/12 4:00 PM

RII-,

M 1, n

A-'v

/1100.J.

u:oi

<fi/J,}/13

-

R	- A

-1MI'\ •,frf

Pr?-

'-	,	t1

---Lsf,

'M ..,OftJ

I  M 1MoA	.

...

I

- -,

I! M	1f."'.;

M	-c,

'R-j

RR-'

M	£ ''-1

/V\ '-i1

,a	'

/	\j

" I	":J

Client Sample # (s):

.

.¼	,I

Total# of Samples:	ll r ntol

1

Relinquished (Cllent):	'O'

Date:	f.	9/ 3

Time:

Received (Cllent):	'; /fJ1JaAZ11 h

Date:  ff:17ctn"T.

Time:	i 2t101n

Comments:	I	{	I

Page 1 of		pages

OrderID: 372313541

Microbiology Chain of Custody

EMSL Order Number (Lab Use Only):

PHONE:

FAX:

| Sample# Sample Location |  |  |
| --- | --- | --- |
| R- O | 31 |  |

Additional Pages of the Chain of Custody are only necessary if needed for additional sample information

Volume/Area	Date/Time Collected

1S-OL

z

c....

.,.Comments/Special Instructions:

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0001 RR-1 150 |  |  | 372313541-0002 RR-2 150 |  |  | 372313541-0003 RR-3 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Rm 350 |  |  | RM 311 |  |  | RM 302 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 2 | 40 | 13 | - | - | - | 369 | 7530 | 96.5 |
| Basidiospores | 9 | 200 | 65.1 | 2 | 40 | 100 | 3 | 60 | 0.8 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 3 | 60 | 19.5 | - | - | - | 8 | 200 | 2.6 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | 1* | 7* | 2.3 | - | - | - | 2* | 10* | 0.1 |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 15 | 307 | 100 | 2 | 40 | 100 | 382 | 7800 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | 1* | 7* | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0004 RR-4 150 |  |  | 372313541-0005 RR-5 150 |  |  | 372313541-0006 RR-6 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 306 |  |  | RM 306A |  |  | RM 303 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | 1 | 20 | 2 | 1 | 20 | 1.8 |
| Aspergillus/Penicillium | 150 | 3060 | 96.8 | 42 | 860 | 86 | 22 | 450 | 39.5 |
| Basidiospores | - | - | - | 1 | 20 | 2 | 1 | 20 | 1.8 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 5 | 100 | 3.2 | 7 | 100 | 10 | 32 | 650 | 57 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 155 | 3160 | 100 | 51 | 1000 | 100 | 56 | 1140 | 100 |
| Hyphal Fragment | 1 | 20 | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 2 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0007 RR-7 150 |  |  | 372313541-0008 RR-8 150 |  |  | 372313541-0009 RR-9 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM G1 |  |  | RM 304 |  |  | Hall RM 323 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 20 | 410 | 71.1 | 1 | 20 | 13.6 | 40 | 820 | 84.8 |
| Basidiospores | 2 | 40 | 6.9 | 4 | 80 | 54.4 | 2 | 40 | 4.1 |
| Bipolaris++ | 1* | 7* | 1.2 | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 7 | 100 | 17.3 | 2 | 40 | 27.2 | 5 | 100 | 10.3 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | 1 | 20 | 3.5 | 1* | 7* | 4.8 | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | 1* | 7* | 0.7 |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 31 | 577 | 100 | 8 | 147 | 100 | 48 | 967 | 100 |
| Hyphal Fragment | 1 | 20 | - | 1 | 20 | - | 1 | 20 | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 3 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0010 RR-10 150 |  |  | 372313541-0011 RR-11 150 |  |  | 372313541-0012 RR-12 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hall RM 311 |  |  | RM 207 |  |  | RM 201A |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | - | - | - | 45 | 920 | 52.9 | 62 | 1300 | 80.2 |
| Basidiospores | 3 | 60 | 75 | 3 | 60 | 3.4 | 3 | 60 | 3.7 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 37 | 760 | 43.7 | 8 | 200 | 12.3 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | 1 | 20 | 25 | - | - | - | 1 | 20 | 1.2 |
| Pithomyces++ | - | - | - | - | - | - | 1 | 20 | 1.2 |
| Rust | - | - | - | - | - | - | 1 | 20 | 1.2 |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 4 | 80 | 100 | 85 | 1740 | 100 | 76 | 1620 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0013 RR-13 150 |  |  | 372313541-0014 RR-14 150 |  |  | 372313541-0015 RR-15 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 202 |  |  | Hall RM 212 + 213 |  |  | RM 230 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 420 | 8570 | 96.5 | 42 | 860 | 91.5 | 18 | 370 | 75.5 |
| Basidiospores | 2 | 40 | 0.5 | 1 | 20 | 2.1 | 6 | 100 | 20.4 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 13 | 270 | 3 | 2 | 40 | 4.3 | 1 | 20 | 4.1 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | 1 | 20 | 2.1 | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 435 | 8880 | 100 | 46 | 940 | 100 | 25 | 490 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | 1 | 20 | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 2 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0016 RR-16 150 |  |  | 372313541-0017 RR-17 150 |  |  | 372313541-0018 RR-18 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 206 |  |  | RM 205 |  |  | RM 201B |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | - | - | - | 29 | 590 | 85.5 | 92 | 1900 | 96 |
| Basidiospores | 1 | 20 | 100 | 4 | 80 | 11.6 | 1 | 20 | 1 |
| Bipolaris++ | - | - | - | - | - | - | 1 | 20 | 1 |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 1 | 20 | 2.9 | 1 | 20 | 1 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | 1 | 20 | 1 |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 1 | 20 | 100 | 34 | 690 | 100 | 96 | 1980 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 1 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0019 RR-19 150 |  |  | 372313541-0020 RR-20 150 |  |  | 372313541-0021 RR-21 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 204 |  |  | Hall RM 216 |  |  | RM 100 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | - | - | - | 27 | 550 | 87.3 | 83 | 1700 | 97.3 |
| Basidiospores | 1 | 20 | 100 | 1 | 20 | 3.2 | 1 | 20 | 1.1 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 2 | 40 | 6.3 | 1 | 20 | 1.1 |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | 1 | 20 | 3.2 | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | 1* | 7* | 0.4 |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 1 | 20 | 100 | 31 | 630 | 100 | 86 | 1747 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | 1* | 7* | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0022 RR-22 150 |  |  | 372313541-0023 RR-23 150 |  |  | 372313541-0024 RR-24 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 101A |  |  | RM 105 |  |  | RM 102 |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 39 | 800 | 97.6 | 16 | 330 | 62.3 | - | - | - |
| Basidiospores | - | - | - | - | - | - | 1 | 20 | 100 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | 8 | 200 | 37.7 | - | - | - |
| Curvularia | - | - | - | - | - | - | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | 1 | 20 | 2.4 | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 40 | 820 | 100 | 24 | 530 | 100 | 1 | 20 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 2 | - | - | 2 | - | - | 1 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0025 RR-25 150 |  |  | 372313541-0026 RR-26 150 |  |  | 372313541-0027 RR-27 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | RM 115 |  |  | RM 103 |  |  | RM 101B |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 2 | 40 | 25 | 70 | 1400 | 77.1 | 32 | 650 | 91.5 |
| Basidiospores | 2 | 40 | 25 | - | - | - | 1 | 20 | 2.8 |
| Bipolaris++ | - | - | - | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | 3 | 60 | 37.5 | 20 | 410 | 22.6 | 2 | 40 | 5.6 |
| Curvularia | - | - | - | 1* | 7* | 0.4 | - | - | - |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | 1 | 20 | 12.5 | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 8 | 160 | 100 | 91 | 1817 | 100 | 35 | 710 | 100 |
| Hyphal Fragment | - | - | - | 1 | 20 | - | - | - | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 1 | - | - | 2 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory

| Lab Sample Number: Client Sample ID: Volume (L): Sample Location: | 372313541-0028 RR-28 150 |  |  | 372313541-0029 RR-29 150 |  |  | 372313541-0030 RR-30 150 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hall RM 118 |  |  | Hall RM 101A |  |  | Outside |  |  |
| Spore Types | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total | Raw Count | Count/m³ | % of Total |
| Alternaria (Ulocladium) | - | - | - | - | - | - | - | - | - |
| Ascospores | - | - | - | - | - | - | - | - | - |
| Aspergillus/Penicillium | 23 | 470 | 92.2 | - | - | - | 41 | 840 | 95.5 |
| Basidiospores | 1 | 20 | 3.9 | 1 | 20 | 100 | 1 | 20 | 2.3 |
| Bipolaris++ | 1 | 20 | 3.9 | - | - | - | - | - | - |
| Chaetomium++ | - | - | - | - | - | - | - | - | - |
| Cladosporium | - | - | - | - | - | - | - | - | - |
| Curvularia | - | - | - | - | - | - | 1 | 20 | 2.3 |
| Epicoccum | - | - | - | - | - | - | - | - | - |
| Fusarium++ | - | - | - | - | - | - | - | - | - |
| Ganoderma | - | - | - | - | - | - | - | - | - |
| Myxomycetes++ | - | - | - | - | - | - | - | - | - |
| Pithomyces++ | - | - | - | - | - | - | - | - | - |
| Rust | - | - | - | - | - | - | - | - | - |
| Scopulariopsis/Microascus | - | - | - | - | - | - | - | - | - |
| Stachybotrys/Memnoniella | - | - | - | - | - | - | - | - | - |
| Unidentifiable Spores | - | - | - | - | - | - | - | - | - |
| Zygomycetes | - | - | - | - | - | - | - | - | - |
| Total Fungi | 25 | 510 | 100 | 1 | 20 | 100 | 43 | 880 | 100 |
| Hyphal Fragment | - | - | - | - | - | - | 1 | 20 | - |
| Insect Fragment | - | - | - | - | - | - | - | - | - |
| Pollen | - | - | - | - | - | - | - | - | - |
| Analyt. Sensitivity 600x | - | 20 | - | - | 20 | - | - | 20 | - |
| Analyt. Sensitivity 300x | - | 7* | - | - | 7* | - | - | 7* | - |
| Skin Fragments (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Fibrous Particulate (1-4) | - | 1 | - | - | 1 | - | - | 1 | - |
| Background (1-5) | - | 2 | - | - | 1 | - | - | 2 | - |

++ Includes other spores with similar morphology; see EMSL's fungal glossary for each specific category.

No discernable field blank was submitted with this group of samples.

Vincent Iuzzolino, M.S., Laboratory Manager or other Approved Signatory