## Sheet1
Tracking Number | Abated? | Location Name | Location Address | Statute Rule | Legal Text | Infraction Location | Infraction Description>
FPVIO-24-1726768008 | FALSE | 240 Frisch Court, F&M Paramus Realty(Common Area) | 240 Frisch Court, F&M Paramus Realty(Common Area) | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Landing between 2nd and 3rd floor | Emergency egress lighting shall be maintained>
FPVIO-24-1726768354 | FALSE | Department of Children and Families | 240 Frisch Court | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Electric room close to elevators | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726767903 | FALSE | 240 Frisch Court, F&M Paramus Realty(Common Area) | 240 Frisch Court, F&M Paramus Realty(Common Area) | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | 3rd floor near elevators | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726767945 | FALSE | 240 Frisch Court, F&M Paramus Realty(Common Area) | 240 Frisch Court, F&M Paramus Realty(Common Area) | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | 3rd floor stairwell near elevators | Storage not permitted in means of egress>
FPVIO-24-1723653849 | FALSE | UFC Gym | UFC Gym | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. |  | Means of egress shall not be obstructed.>
FPVIO-24-1723651205 | FALSE | Christie's International Real Estate | Christie's International Real Estate | 906.6 | Portable fire extinguishers shall not be obstructed or obscured from view. In rooms or areas in which visual obstruction cannot be completely avoided, means shall be provided to indicate the locations of extinguishers. | Electrical room | Fire extinguisher access shall not be obstructed>
FPVIO-24-1726852144 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire Lane shall not be obstructed. 22 cars improperly parked throughout property>
FPVIO-24-1723653656 | FALSE | UFC Gym | UFC Gym | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Muay Thai room | Exit/ Direction Signs shall be maintained>
FPVIO-24-1723652850 | FALSE | UFC Gym | UFC Gym | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Men's locker room | Exit/ Direction Signs shall be maintained>
FPVIO-24-1726767358 | FALSE | 240 Frisch Court, F&M Paramus Realty(Common Area) | 240 Frisch Court, F&M Paramus Realty(Common Area) | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | main entrance | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1723661662 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 903.5 | Sprinkler systems shall be tested and maintained in accordance with Section 901. | 2nd floor elevator landing | Missing sprinkler concealer caps shall be replaced./RN>
FPVIO-24-1723661391 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 903.5 | Sprinkler systems shall be tested and maintained in accordance with Section 901. | outside of 205 | Missing sprinkler concealer caps shall be replaced./RN>
FPVIO-24-1723667445 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 315.3.3 | Combustible material shall not be stored in boiler rooms, mechanical rooms, electrical equipment rooms or in fire command centers as specified in Section 508.1.5. | 1st floor boiler room | Storage not permitted in utility rooms/RN>
FPVIO-24-1723667384 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | 1st floor electrical room | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1723660612 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Breakroom | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1726757755 | FALSE | Metropolitan Eye Care | Metropolitan Eye Care | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | near other waiting room/ exit | Emergency egress lighting shall be maintained>
FPVIO-24-1726757994 | FALSE | Metropolitan Eye Care | Metropolitan Eye Care | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | left side of reception desk | Emergency egress lighting shall be maintained>
FPVIO-24-1723660493 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. |  | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1723654509 | FALSE | Go Low Indoor Golf | Go Low Indoor Golf | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Throughout | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1727205094 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire Lane shall not be obstructed. 9 cars improperly parked throughout the lot>
FPVIO-24-1729279799 | FALSE | True Light Presbyterian Church | True Light Presbyterian Church | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required Per Annual Sprinkler Report conducted on 10/11/24, Hydrostatic Test must be performed by licensed contractor on FDC>
FPVIO-24-00143 | FALSE | The Primrose School | 639 Paramus Road | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required. All sprinkler deficiencies must be repaired.>
FPVIO-24-1723649215 | FALSE | Victoria's Nursery | Victoria's Nursery | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | front entrance | Exit/ Direction Signs shall be maintained>
FPVIO-24-1730305233 | FALSE | Lenscrafters | Lenscrafters | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required Sprinkler Report from 9/2024 Annual Sprinkler test states multiple deficiencies. Deficiencies must be addressed and repaired within two weeks>
FPVIO-24-1729881551 | FALSE | Barnes & Noble 3448 | Barnes & Noble 3448 | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required Report from 10/3/2024 states multiple deficiencies in system. Deficiencies must be addressed and repaired>
FPVIO-24-1729882967 | FALSE | West Elm | West Elm | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required Sprinkler report from 3/2024 states multiple deficiencies. deficiencies must be repaired>
FPVIO-24-1728663071 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Kiosks outside of Claire's | Means of egress shall not be obstructed.>
FPVIO-24-1723651114 | FALSE | Christie's International Real Estate | Christie's International Real Estate | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Electrical room | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1727376680 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire Lane shall not be obstructed. 22 cars improperly parked throughout lot.>
FPVIO-24-1723651183 | FALSE | Christie's International Real Estate | Christie's International Real Estate | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Electrical room | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1727290789 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire Lane shall not be obstructed/RN>
FPVIO-24-00137 | FALSE | Burlington Center Mall (Common Areas - Store #6) | 651 Route 17 | 901.6 | Fire detection, alarm, and extinguishing systems, mechanical smoke exhaust systems, and smoke and heat vents whether in a permanent structure or a mobile enclosed unit shall be maintained in an operative condition at all times, and shall be replaced or repaired where defective. | South most riser in Burlington Store | Fire protection systems shall be maintained in operative condition at all times, repair or replace where defective. OS&Y valve leaking>
FPVIO-24-1723649431 | FALSE | Victoria's Nursery | Victoria's Nursery | 313.1 | Fueled equipment including, but not limited to, motorcycles, mopeds, lawn-care equipment, portable generators and portable cooking equipment, shall not be stored, operated or repaired within a building. /RNExceptions: /RN1. Buildings or rooms constructed for such use in accordance with the building subcode of the Uniform Construction Code. /RN2. Where allowed by Section 314. /RN3. Storage of equipment utilized for maintenance purposes is allowed in approved locations where the aggregate fuel capacity of the stored equipment does not exceed 10 gallons (38 L) and the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. | Weedwacker in back storage area | Fueled equipment stored indoors shall have fuel tanks emptied.>
FPVIO-24-00138 | FALSE | Burlington Center Mall (Common Areas - Store #6) | 651 Route 17 | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. | South end of parking lot near Pet Goods | Fire Protection system maintenance required. Yard hydrant in south lot must be repaired>
FPVIO-24-1723649494 | FALSE | Victoria's Nursery | Victoria's Nursery | 906.6 | Portable fire extinguishers shall not be obstructed or obscured from view. In rooms or areas in which visual obstruction cannot be completely avoided, means shall be provided to indicate the locations of extinguishers. |  | Fire extinguisher access shall not be obstructed>
FPVIO-24-1726586965 | FALSE | Bank of America | Bank of America | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1726586973 | FALSE | Bank of America | Bank of America | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. |  | Fire alarm maintenance required./RN old monitoring company reports they are receiving signals still. Have new monitoring company forward a certificate to fire prevention that states the alarm is being monitored.>
FPVIO-24-1726584807 | FALSE | Smile Care Direct Group | 2 Forest Avenue | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1726586943 | FALSE | Bank of America | Bank of America | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1726587159 | FALSE | Bank of America | Bank of America | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Electrical room | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726591339 | FALSE | Dunkin Donuts | Dunkin Donuts | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. |  | Storage not permitted in means of egress>
FPVIO-24-1723735132 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Fire Panel room | Emergency egress lighting shall be maintained>
FPVIO-24-1726587714 | FALSE | Bank of America | Bank of America | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Breakroom | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726591323 | FALSE | Dunkin Donuts | Dunkin Donuts | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | back exit | Exit/ Direction Signs shall be maintained>
FPVIO-24-1726584448 | FALSE | Smile Care Direct Group | 2 Forest Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1726502390 | FALSE | Balanced Body Holistic Healthcare | Balanced Body Holistic Healthcare | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1726503074 | FALSE | North Jersey Health & Wellness LLC | North Jersey Health & Wellness LLC | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1726500804 | FALSE | Silicom | 4 Forest Avenue | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1726501029 | FALSE | Forest Recovery and Psychiatic Group | 4 Forest Avenue | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1726503654 | FALSE | AC Dental of Hackensack & Paramus | AC Dental of Hackensack & Paramus | 806.2 | Artificial decorative vegetation shall meet the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701. Meeting the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be documented and certified by the manufacturer in an approved manner. Alternatively, the artificial decorative vegetation item shall be tested in accordance with NFPA 289, using the 20 kW ignition source, and shall have a maximum heat release rate of 100 kW. |  | Artificial Vegitation must meet NFPA 701 Flame Spread Rating/RN>
FPVIO-24-1726516568 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. | Parking lot and access road | Fire Lane shall not be obstructed. 6 cars improperly parked throughout the property.>
FPVIO-24-1726584434 | FALSE | Smile Care Direct Group | 2 Forest Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723735218 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | 1st floor storage room near fire panel room | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1726505850 | FALSE | Rad Com | Rad Com | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1726592247 | FALSE | Hair & Beauty Lounge | Hair & Beauty Lounge | 605.4 | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with the electrical subcode of the Uniform Construction Code shall be prohibited. | First room on left | Multi-plug adapters prohibited/RN>
FPVIO-24-1726597512 | FALSE | BTR Advisers | 52 Forest Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | outside of Robert Lax office | Emergency egress lighting shall be maintained>
FPVIO-24-1726597743 | FALSE | 52 Forest Realty Association | 52 Forest Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 1st floor landing | Emergency egress lighting shall be maintained>
FPVIO-24-1726597261 | FALSE | Certified Financial Services (CFS) - Guardian | 52 Forest Avenue | 806.2 | Artificial decorative vegetation shall meet the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701. Meeting the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be documented and certified by the manufacturer in an approved manner. Alternatively, the artificial decorative vegetation item shall be tested in accordance with NFPA 289, using the 20 kW ignition source, and shall have a maximum heat release rate of 100 kW. |  | Artificial Vegitation must meet NFPA 701 Flame Spread Rating/RN>
FPVIO-24-1726597308 | FALSE | Certified Financial Services (CFS) - Guardian | 52 Forest Avenue | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Electrical room | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726676366 | FALSE | Church of The Savior | 643 Forest Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | exit near pastors office | Emergency egress lighting shall be maintained>
FPVIO-24-1726677724 | FALSE | Church of The Savior | 643 Forest Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723667490 | FALSE | Paramus Place aka Paul-Central Corp | Paramus Place aka Paul-Central Corp | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | hallway outside 104 | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726676512 | FALSE | Church of The Savior | 643 Forest Avenue | 605.5 | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | Mrs. Morrow's classroom | Extension cords shall not be utilized as permanant wiring./RN>
FPVIO-24-1726677683 | FALSE | Church of The Savior | 643 Forest Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1726597022 | FALSE | MetroMultimedia Services, Inc | 52 Forest Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | rear exit | Emergency egress lighting shall be maintained>
FPVIO-24-1726592520 | FALSE | Bee Nails and Spa | Bee Nails and Spa | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1726592840 | FALSE | Forest Cleaners | Forest Cleaners | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | fitting room | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1726592277 | FALSE | Hair & Beauty Lounge | Hair & Beauty Lounge | 806.2 | Artificial decorative vegetation shall meet the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701. Meeting the flame propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be documented and certified by the manufacturer in an approved manner. Alternatively, the artificial decorative vegetation item shall be tested in accordance with NFPA 289, using the 20 kW ignition source, and shall have a maximum heat release rate of 100 kW. | First room on left | Artificial Vegitation must meet NFPA 701 Flame Spread Rating/RN>
FPVIO-24-1726592480 | FALSE | Bee Nails and Spa | Bee Nails and Spa | 605.5 | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | laundry room | Extension cords shall not be utilized as permanant wiring./RN>
FPVIO-24-1726593467 | FALSE | Fuel 4 | Fuel 4 | 313.1 | Fueled equipment including, but not limited to, motorcycles, mopeds, lawn-care equipment, portable generators and portable cooking equipment, shall not be stored, operated or repaired within a building. /RNExceptions: /RN1. Buildings or rooms constructed for such use in accordance with the building subcode of the Uniform Construction Code. /RN2. Where allowed by Section 314. /RN3. Storage of equipment utilized for maintenance purposes is allowed in approved locations where the aggregate fuel capacity of the stored equipment does not exceed 10 gallons (38 L) and the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. |  | Fueled equipment stored indoors shall have fuel tanks emptied.>
FPVIO-24-1726596802 | FALSE | Proviser Financial | 52 Forest Avenue | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | server room | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726596931 | FALSE | MetroMultimedia Services, Inc | 52 Forest Avenue | 605.5 | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | reception | Extension cords shall not be utilized as permanant wiring./RN>
FPVIO-24-1723725394 | FALSE | International Brotherhood of Electrical Workers | International Brotherhood of Electrical Workers | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | throughout | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1726594408 | FALSE | Hamilton Behavioral Health | Hamilton Behavioral Health | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1730305330 | FALSE | Lenscrafters | Lenscrafters | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. |  | Fire alarm maintenance required./RN Annual Fire Alarm test from 9/2024 states deficiency. Have deficiencies addressed and repaired in two weeks>
FPVIO-24-1732033181 | FALSE | Grand Lux Cafe Level 2 R1 | Grand Lux Cafe Level 2 R1 | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. |  | Fire alarm maintenance required./RN>
FPVIO-24-1731952492 | FALSE | Capital Grille G02 | Capital Grille G02 | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Stairwell | Means of egress shall not be obstructed.>
FPVIO-24-1731952392 | FALSE | Capital Grille G02 | Capital Grille G02 | 904.5.1 | Systems shall be inspected and tested for proper operation at six-month intervals. Tests shall include a check of the detection system, alarms and releasing devices, including manual stations and other associated equipment. Extinguishing system units shall be weighed and the required amount of agent verified. Stored pressure-type units shall be checked for the required pressure. The cartridge of cartridge-operated units shall be weighed and replaced at intervals indicated by the manufacturer. |  | Wet Chemical Suppression System inspection required (6 Months)>
FPVIO-24-1731952403 | FALSE | Capital Grille G02 | Capital Grille G02 | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Upstairs hallway | Means of egress shall not be obstructed.>
FPVIO-24-1723128446 | FALSE | Bahama Breeze | Bahama Breeze | 912.7 | Fire department connections shall be periodically inspected, tested and maintained in accordance with NFPA 25. Records of inspection, testing and maintenance shall be maintained. | outside | FDC Caps missing must be replaced>
FPVIO-24-1723055253 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 5 near Nordstrom rack | Storage not permitted in means of egress>
FPVIO-24-1723055152 | FALSE | J. Crew #117 | 1 Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 5 | Storage not permitted in means of egress>
FPVIO-24-1723055084 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 5 | Storage not permitted in means of egress>
FPVIO-24-1730909228 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Across from Marshall's Dock, Whole Foods Dock | Storage not permitted in means of egress>
FPVIO-24-1730909527 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1 | An exit shall not be utilized for any purpose that interferes with its function as a means of egress, except as otherwise approved. The means of egress from each part of the structure, including exits, stairways, egress doors and any panic hardware installed thereon, aisles, corridors, passageways and similar elements of the means of egress, shall at all times be maintained in a safe condition and available for immediate utilization and free of all obstructions. Security devices affecting means of egress shall be subject to approval. |  | Means of Egress shall be maintained at all times>
FPVIO-24-1723483859 | FALSE | Shin-Etsu Silicones of America | Shin-Etsu Silicones of America | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Lab area | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1723487181 | FALSE | Sarku Japan |  | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. |  | Storage not permitted in means of egress>
FPVIO-24-1723483913 | FALSE | Shin-Etsu Silicones of America | Shin-Etsu Silicones of America | 903.5 | Sprinkler systems shall be tested and maintained in accordance with Section 901. | outside lab entrance | Missing sprinkler concealer caps shall be replaced./RN>
FPVIO-24-1730911669 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 1 upper | Storage not permitted in means of egress>
FPVIO-24-1731082496 | FALSE | Miller's Ale House | Miller's Ale House | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Patio entrance | Exit/ Direction Signs shall be maintained>
FPVIO-24-1731082386 | FALSE | Miller's Ale House | Miller's Ale House | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Foyer entrance | Exit/ Direction Signs shall be maintained>
FPVIO-24-1731082468 | FALSE | Miller's Ale House | Miller's Ale House | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Deck | Emergency egress lighting shall be maintained>
FPVIO-24-00148 | FALSE | Paramus Southbound Property LLC | 309 Route 17 South | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required./RN/RNRepairs must be made to sprinkler system, backflow and hydrant>
FPVIO-24-1723147164 | FALSE | Olive Garden | Olive Garden | 609.3.3.1.1 | Where a cleaning schedule is not on file, the fire official shall require a schedule to be submitted, indicating the method of cleaning and the time intervals between cleanings. | Hood above fryer | Cleaning schedule shall be conducted on a monthly basis on hood above fryer>
FPVIO-24-1730913024 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Crumbl Cookie exit | Storage not permitted in means of egress>
FPVIO-24-1730912283 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 703.2 | Opening protectives shall be maintained in an operative condition in accordance with NFPA 80. Where allowed by the fire code official, the application of field-applied labels associated with the maintenance of opening protectives shall follow the requirements of the approved third-party certification organization accredited for listing the opening protective. Fire doors and smoke barrier doors shall not be blocked or obstructed, or otherwise made inoperable. Door stops, wedges and other unapproved hold-open devices shall be prohibited. Fusible links shall be replaced promptly whenever fused or damaged. Fire door assemblies shall not be modified. | Corridor 5 | Fire Doors shall not be blocked open or obstructed.>
FPVIO-24-1730913623 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 703.2.3 | Swinging fire doors shall close from the full-open position and latch automatically. The door closer shall exert enough force to close and latch the door from any partially open position. | near Lincoln tech corridor, outside bldg 200 stair 1 room 8 | Door not closing/latching. must self close>
FPVIO-24-1730915347 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 703.2 | Opening protectives shall be maintained in an operative condition in accordance with NFPA 80. Where allowed by the fire code official, the application of field-applied labels associated with the maintenance of opening protectives shall follow the requirements of the approved third-party certification organization accredited for listing the opening protective. Fire doors and smoke barrier doors shall not be blocked or obstructed, or otherwise made inoperable. Door stops, wedges and other unapproved hold-open devices shall be prohibited. Fusible links shall be replaced promptly whenever fused or damaged. Fire door assemblies shall not be modified. | Corridor 3 to loading dock 4 | Fire Doors shall not be blocked open or obstructed.>
FPVIO-24-1730915555 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 3 | Storage not permitted in means of egress>
FPVIO-24-1730914874 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Corridor 1 lower near stair 1 | Storage not permitted in means of egress>
FPVIO-24-1730915225 | FALSE | The Outlets at Bergen Town Center | The Outlets at Bergen Town Center | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | Lower corridor 2 | Storage not permitted in means of egress>
FPVIO-24-1724680863 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Band room | Emergency egress lighting shall be maintained>
FPVIO-24-1724681065 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 500 hallway by the front entrance | Emergency egress lighting shall be maintained>
FPVIO-24-1724680466 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | stage garage door | Emergency egress lighting shall be maintained>
FPVIO-24-1724680602 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | boys dressing room | Emergency egress lighting shall be maintained>
FPVIO-24-1724681368 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | cardio room | Emergency egress lighting shall be maintained>
FPVIO-24-1724684034 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | AB Gym (4) | Emergency egress lighting shall be maintained>
FPVIO-24-1724684766 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 100 hallway | Emergency egress lighting shall be maintained>
FPVIO-24-1724681961 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | boys locker room | Emergency egress lighting shall be maintained>
FPVIO-24-1724682377 | FALSE | Paramus High School | 99 E. Century Road | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | middle gym exterior door by boys locker room | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724680334 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Auditorium side wall | Emergency egress lighting shall be maintained>
FPVIO-24-1724352191 | FALSE | Abe Elson, M.D. | Abe Elson, M.D. | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. |  | Emergency egress lighting shall be maintained>
FPVIO-24-1724352978 | FALSE | Stephen J McIlveen, M.D. | Stephen J McIlveen, M.D. | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | exam room 2 | Emergency egress lighting shall be maintained>
FPVIO-24-1724351819 | FALSE | Roger G. Pollock, MD | Roger G. Pollock, MD | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | main entrance | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724352150 | FALSE | Abe Elson, M.D. | Abe Elson, M.D. | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724081784 | FALSE | Bagel Supreme | 425 Farview Avenue | 906.9 | The installation of portable fire extinguishers shall be in accordance with Sections 906.9.1 through 906.9.3. |  | Fire Extinguisher shall be properly mounted>
FPVIO-24-1724680029 | FALSE | Paramus High School | 99 E. Century Road | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | main gym | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724680099 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | main gym (4) | Emergency egress lighting shall be maintained>
FPVIO-24-1724081767 | FALSE | Bagel Supreme | 425 Farview Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724081755 | FALSE | Bagel Supreme | 425 Farview Avenue | 904.12.5 | Portable fire extinguishers shall be provided within a 30-foot (9144 mm) distance of travel from commercial-type cooking equipment. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K rated portable extinguisher in accordance with Section 904.12.5.1 or 904.12.5.2, as applicable. |  | Class K Extinguisher Required. needs to be inspected and mounted>
FPVIO-24-1724685231 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Library (4) | Emergency egress lighting shall be maintained>
FPVIO-24-00122 | FALSE | 736 Route 17 | 736 Route 17 | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Forward a copy of Annual Sprinkler Test Report to Fire Prevention>
FPVIO-24-00121 | FALSE | Yeshivat Noam Middle School | Yeshivat Noam Middle School | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724691601 | FALSE | Paramus High School | 99 E. Century Road | 1010.1.9 | Egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | Receiving exterior door | Means of egress shall be readily openable>
FPVIO-24-00120 | FALSE | Yeshivat Noam Middle School | Yeshivat Noam Middle School | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724787888 | FALSE | Borough of Paramus- Borough Hall | 1 Jockish Square | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | janitorial closet | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1724788335 | FALSE | Borough of Paramus- Borough Hall | 1 Jockish Square | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | emergency light 13, tax/health stairwell | Emergency egress lighting shall be maintained>
FPVIO-24-00119 | FALSE | Yeshivat Noam | Yeshivat Noam | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724774717 | FALSE | Zara USA Inc Level 1 1046, S1080, S1033 | One Garden State Plaza | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Electrical | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724690664 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | stairwell 4 top | Emergency egress lighting shall be maintained>
FPVIO-24-1724687456 | FALSE | Paramus High School | 99 E. Century Road | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | 300 hallway by 400 intersection | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1724688096 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 200 vestibule | Emergency egress lighting shall be maintained>
FPVIO-24-1724685553 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | ecc hallway and classrooms | Emergency egress lighting shall be maintained>
FPVIO-24-1724685887 | FALSE | Paramus High School | 99 E. Century Road | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | ECC hallway | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724688184 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Board office vestibule | Emergency egress lighting shall be maintained>
FPVIO-24-1724690045 | FALSE | Paramus High School | 99 E. Century Road | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Boiler room | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724690530 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 902 | Emergency egress lighting shall be maintained>
FPVIO-24-1724688319 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Board office Mechanical pit | Emergency egress lighting shall be maintained>
FPVIO-24-1724688849 | FALSE | Paramus High School | 99 E. Century Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | 600 hallway by stair 3 | Emergency egress lighting shall be maintained>
FPVIO-24-1724175743 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | hallway, near nurses office | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724166481 | FALSE | Annunciation Parish Center | Annunciation Parish Center | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | meter room in basement | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1724176165 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 404.2.1 | Fire evacuation plans shall include the following: /RN1. Emergency egress or escape routes and whether evacuation of the building is to be complete by selected floors or areas only or with a defend-in-place response. /RN2. Procedures for employees who must remain to operate critical equipment before evacuating. /RN3. Procedures for the use of elevators to evacuate the building where occupant evacuation elevators complying with the building subcode of the Uniform Construction Code are provided. /RN4. Procedures for assisted rescue for persons unable to use the general means of egress unassisted. /RN5. Procedures for accounting for employees and occupants after evacuation has been completed. /RN6. Identification and assignment of personnel responsible for rescue or emergency medical aid. /RNEMERGENCY PLANNING AND PREPAREDNESS /RN7. The preferred and any alternative means of notifying occupants of a fire or emergency. /RN8. The preferred and any alternative means of reporting fires and other emergencies to the fire department or designated emergency response organization. /RN9. Identification and assignment of personnel who can be contacted for further information or explanation of duties under the plan. /RN10. A description of the emergency voice/alarm communication system alert tone and preprogrammed voice messages, where provided. | SGI room G8; C1; D9; D7; F2 | Egress Maps Required.>
FPVIO-24-1724176044 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | hallway to media center | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724166386 | FALSE | Annunciation Parish Center | Annunciation Parish Center | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | stairs to basement | Emergency egress lighting shall be maintained>
FPVIO-24-1724089987 | FALSE | State Farm Insurance | State Farm Insurance | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | main exit | Exit/ Direction Signs shall be maintained>
FPVIO-24-00126 | FALSE | Abe Elson, M.D. | Abe Elson, M.D. | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | 2024 Registration | Failure to obtain annual fire prevention registration.>
FPVIO-24-00125 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Both Gyms | Means of egress including the exit discharge shall be illuminated at all times. Emergency lights must be added to both gyms.>
FPVIO-24-1724176437 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Storage area for room A 2013 9 | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724181237 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | between main gym and boys locker room | Exit/ Direction Signs shall be maintained>
FPVIO-24-1724181067 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | girls, locker room hallway | Means of egress shall not be obstructed.>
FPVIO-24-1724184194 | FALSE | Buehler Challenger Science Center | Buehler Challenger Science Center | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724181360 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | boys, locker room hallway | Emergency egress lighting shall be maintained>
FPVIO-24-1724180803 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | hallway by the auxiliary gym | Emergency egress lighting shall be maintained>
FPVIO-24-1724177072 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 605.4.2 | Relocatable power taps shall be directly connected to a permanently installed receptacle. | room e-6 | Power strips must not be piggy backed>
FPVIO-24-1724176456 | FALSE | Assyrian Orthodox Church | 644 Paramus Road | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724177485 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Power room E hallway | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724177331 | FALSE | Eastbrook Middle School | 190 Spring Valley Road | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | Storage for E8 | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-00127 | FALSE | Abe Elson, M.D. | Abe Elson, M.D. | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | 2024 Registration | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-24-1724351005 | FALSE | Advance Medical Group | Advance Medical Group | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1724085031 | FALSE | The Frisch School | 120 W. Century Road | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724350587 | FALSE | Advanced Women's Healthcare PA | Advanced Women's Healthcare PA | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1724351139 | FALSE | Bergen Medical Center Building | Bergen Medical Center Building | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | 2nd floor electrical room | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724083383 | FALSE | Miller's Ale House | Miller's Ale House | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724351797 | FALSE | Roger G. Pollock, MD | Roger G. Pollock, MD | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Throughout | Emergency egress lighting shall be maintained>
FPVIO-24-1724085023 | FALSE | The Frisch School | 120 W. Century Road | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724084937 | FALSE | DXL Male | 450 Route 17 | 912.4 | Immediate access to fire department connections shall be maintained at all times and without obstruction by fences, bushes, trees, walls or any other fixed or moveable object. Access to fire department connections shall be approved by the fire chief. /RNException: Fences, where provided with an access gate equipped with a sign complying with the legend requirements of Section 912.5 and a means of emergency operation. The gate and the means of emergency operation shall be approved by the fire chief and maintained operational at all times. |  | Accumulations of vegitation near FDC shall be removed/RN>
FPVIO-24-1724085423 | FALSE | The Frisch School | 120 W. Century Road | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | outside lab 22 | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724086477 | FALSE | The Frisch School | 120 W. Century Road | 605.5 | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | basement storage area | Extension cords shall not be utilized as permanant wiring./RN>
FPVIO-24-1724085917 | FALSE | The Frisch School | 120 W. Century Road | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | hallway by book room | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-00128 | FALSE | New York Bariatric Group | 1 W. Ridgewood Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. |  | Unpaid Registration fee from 11/2023 must be paid >
FPVIO-24-1724086666 | FALSE | The Frisch School | 120 W. Century Road | 906.1 | Portable fire extinguishers shall be installed in all of the following locations: /RN1. In new and existing Group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies. /RNExceptions: /RN1. In Group R-2 occupancies, portable fire extinguishers shall be required only in locations specified in Items 2 through 6 where each dwelling unit is provided with a portable fire extinguisher having a minimum rating of 1-A:10-B:C. /RN2. In Group A, B and E occupancies equipped throughout with quick response sprinklers, portable fire extinguishers shall be required only in locations specified in Items 2 through 6. /RN2. Within 30 feet (9144 mm) of commercial cooking equipment. /RN3. In areas where flammable or combustible liquids are stored, used or dispensed. /RN4. On each floor of structures under construction, except Group R-3 occupancies, in accordance with Section 3315.1. /RN5. Where required by the sections indicated in Table 906.1. /RN6. Special-hazard areas, including but not limited to laboratories, computer rooms and generator rooms, where required by the fire code official. | gym | Fire Extinguishers Required/RN>
FPVIO-24-1724085772 | FALSE | The Frisch School | 120 W. Century Road | 605.5 | Extension cords and flexible cords shall not be a substitute for permanent wiring. Extension cords and flexible cords shall not be affixed to structures, extended through walls, ceilings or floors, or under doors or floor coverings, nor shall such cords be subject to environmental damage or physical impact. Extension cords shall be used only with portable appliances. | maintenance lunch room | Extension cords shall not be utilized as permanant wiring./RN>
FPVIO-24-1724349252 | FALSE | Bergen Medical Center Building | Bergen Medical Center Building | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Electrical Room bariatric group | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724349271 | FALSE | Bergen Medical Center Building | Bergen Medical Center Building | 906.9 | The installation of portable fire extinguishers shall be in accordance with Sections 906.9.1 through 906.9.3. | electrical room bariatric group | Fire Extinguisher shall be properly mounted>
FPVIO-24-1724085637 | FALSE | The Frisch School | 120 W. Century Road | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | kitchen | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724349212 | FALSE | Bergen Medical Center Building | Bergen Medical Center Building | 605.6 | Open junction boxes and open-wiring splices shall be prohibited. Approved covers shall be provided for all switch and electrical outlet boxes. | Electrical Room in Bariatric group ground floor | Open electrical junction boxes/wiring is prohibited./RN>
FPVIO-24-1724788558 | FALSE | Borough of Paramus- Borough Hall | 1 Jockish Square | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | mail room- missing ceiling tiles | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726068964 | FALSE | Steps NY Level 2 B7 | One Garden State Plaza | 5:70-4.9(d) | Effective September 3, 2017, carbon monoxide detection equipment shall be installed in all existing buildings which contain a fuel-burning appliance or have an attached garage. An open parking structure, as defined in the building subcode of the Uniform Construction Code, shall not be deemed to be an attached garage. 1. One- and two-family dwellings: Carbon monoxide detection shall be installed in buildings of Use Groups R-3 and R-4 in accordance with the requirements of N.J.A.C. 5:70-4.19. 2. Carbon monoxide detection equipment shall be installed in the immediate vicinity of each sleeping area in any guestroom or dwelling unit located in a building of Group I-1, R-1 or R-2 occupancies, except as provided in (d)2i or ii below. i. Guestrooms or dwelling units which do not themselves contain a fuel-burning appliance or have an attached garage, but which are located in a building with a fuel-burning appliance or an attached garage, need not be provided with single station carbon monoxide detection equipment provided that: (1) The guestroom or dwelling unit is located more than one story above or below any story which contains a fuel-burning appliance or an attached garage; (2) The guestroom or dwelling unit is not connected by duct work or ventilation shafts to any room containing a fuel-burning appliance or an attached garage and the building has a common area carbon monoxide alarm system with all common area detectors connected to an approved supervisory station or other approved local visual and audible supervisory signal; and (3) Individual detection equipment is located in every room adjacent to the room(s) containing a fuel-burning appliance; and (A) In every corridor, hall or lobby adjacent to such room(s); (B) In the immediate vicinity of any ventilated shaft, including, but not limited to, stair shafts, elevator shafts, ventilation shafts on the story containing the fuel-burning appliance; and (C) On any story within two stories above or below the story containing the fuel-burning appliance. ii. The building is provided with a supervised carbon monoxide detection system. Individual detectors shall be located in every room containing a fuel-burning appliance. All such detectors shall be connected to an approved supervisory station. Carbon monoxide and fire alarms may be incorporated into a common monitored system. 3. Carbon monoxide detection equipment shall be installed in all occupancies other than those listed in (d)2 above in accordance with this paragraph. Systems using detectors shall have a distinct visual and audible notification. When alarms are installed in lieu of detectors, they shall be located such that the audible signal is not less than 15 dB above the average ambient sound level. Carbon monoxide detectors or alarms shall be installed in the immediate vicinity of all potential source(s) of carbon monoxide. i. Carbon monoxide detection equipment shall not be required: (1) In locations, such as repair garages, where the presence of carbon monoxide may be expected as a function of the normal use of the space; (2) In the immediate area of large-drop battery charging; (3) In unconditioned spaces where detectors or alarms may be subject to ambient temperatures outside the device's listed operating range or spaces where exposure to potential contaminants which may adversely affect their operation. For unconditioned spaces that require such detection, detection equipment shall be installed in approved adjacent room(s) or space(s); (4) In other occupiable space(s) not connected by duct work or ventilation shafts to any room containing a fuel-burning appliance or to an attached garage, provided that the building has a common area carbon monoxide detection system with all common area detectors connected to an approved supervisory station or other approved local visual and audible supervisory signal and individual carbon monoxide alarms are located: (A) In every room adjacent to the room(s) containing a fuel-burning appliance, and in every corridor, hall or lobby adjacent to such room(s); (B) In the immediate vicinity of any ventilated shaft, including, but not limited to, stair shafts, elevator shafts, or ventilation shafts on the story containing the fuel-burning appliance; (C) In the first area served by each main duct leaving the area where the appliance is located; and (D) Any story within two stories above or below a story containing a fuel-burning appliance. 4. For carbon monoxide detection systems in occupancies other than those listed in (d)2 above, audible and visual supervisory notification shall only be provided at the detector, control panel and remote annunciator. The balance of the system installation shall comply with NFPA 720 and with the Uniform Construction Code. Carbon monoxide and fire alarms may be incorporated into a common monitored system. 5. Carbon monoxide alarms shall be manufactured, listed and labeled in accordance with UL 2034 and shall be installed and maintained in accordance with the requirements of this section and the edition of NFPA 720 currently referenced in this chapter, as applicable. Carbon monoxide alarms may be battery operated, hard wired or of the plug-in type. Expired alarms shall be immediately replaced. 6. Carbon monoxide detection systems shall comply with the edition of NFPA 720 currently referenced in this chapter. Carbon monoxide detectors shall be listed in accordance with UL 2075. |  | Carbon Monoxide alarms shall be maintained/RN>
FPVIO-24-1723823916 | FALSE | Windsor Prep High School | Windsor Prep High School | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1726068908 | FALSE | Steps NY Level 2 B7 | One Garden State Plaza | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1726068945 | FALSE | Steps NY Level 2 B7 | One Garden State Plaza | 5:70-4.9(d) | Effective September 3, 2017, carbon monoxide detection equipment shall be installed in all existing buildings which contain a fuel-burning appliance or have an attached garage. An open parking structure, as defined in the building subcode of the Uniform Construction Code, shall not be deemed to be an attached garage. 1. One- and two-family dwellings: Carbon monoxide detection shall be installed in buildings of Use Groups R-3 and R-4 in accordance with the requirements of N.J.A.C. 5:70-4.19. 2. Carbon monoxide detection equipment shall be installed in the immediate vicinity of each sleeping area in any guestroom or dwelling unit located in a building of Group I-1, R-1 or R-2 occupancies, except as provided in (d)2i or ii below. i. Guestrooms or dwelling units which do not themselves contain a fuel-burning appliance or have an attached garage, but which are located in a building with a fuel-burning appliance or an attached garage, need not be provided with single station carbon monoxide detection equipment provided that: (1) The guestroom or dwelling unit is located more than one story above or below any story which contains a fuel-burning appliance or an attached garage; (2) The guestroom or dwelling unit is not connected by duct work or ventilation shafts to any room containing a fuel-burning appliance or an attached garage and the building has a common area carbon monoxide alarm system with all common area detectors connected to an approved supervisory station or other approved local visual and audible supervisory signal; and (3) Individual detection equipment is located in every room adjacent to the room(s) containing a fuel-burning appliance; and (A) In every corridor, hall or lobby adjacent to such room(s); (B) In the immediate vicinity of any ventilated shaft, including, but not limited to, stair shafts, elevator shafts, ventilation shafts on the story containing the fuel-burning appliance; and (C) On any story within two stories above or below the story containing the fuel-burning appliance. ii. The building is provided with a supervised carbon monoxide detection system. Individual detectors shall be located in every room containing a fuel-burning appliance. All such detectors shall be connected to an approved supervisory station. Carbon monoxide and fire alarms may be incorporated into a common monitored system. 3. Carbon monoxide detection equipment shall be installed in all occupancies other than those listed in (d)2 above in accordance with this paragraph. Systems using detectors shall have a distinct visual and audible notification. When alarms are installed in lieu of detectors, they shall be located such that the audible signal is not less than 15 dB above the average ambient sound level. Carbon monoxide detectors or alarms shall be installed in the immediate vicinity of all potential source(s) of carbon monoxide. i. Carbon monoxide detection equipment shall not be required: (1) In locations, such as repair garages, where the presence of carbon monoxide may be expected as a function of the normal use of the space; (2) In the immediate area of large-drop battery charging; (3) In unconditioned spaces where detectors or alarms may be subject to ambient temperatures outside the device's listed operating range or spaces where exposure to potential contaminants which may adversely affect their operation. For unconditioned spaces that require such detection, detection equipment shall be installed in approved adjacent room(s) or space(s); (4) In other occupiable space(s) not connected by duct work or ventilation shafts to any room containing a fuel-burning appliance or to an attached garage, provided that the building has a common area carbon monoxide detection system with all common area detectors connected to an approved supervisory station or other approved local visual and audible supervisory signal and individual carbon monoxide alarms are located: (A) In every room adjacent to the room(s) containing a fuel-burning appliance, and in every corridor, hall or lobby adjacent to such room(s); (B) In the immediate vicinity of any ventilated shaft, including, but not limited to, stair shafts, elevator shafts, or ventilation shafts on the story containing the fuel-burning appliance; (C) In the first area served by each main duct leaving the area where the appliance is located; and (D) Any story within two stories above or below a story containing a fuel-burning appliance. 4. For carbon monoxide detection systems in occupancies other than those listed in (d)2 above, audible and visual supervisory notification shall only be provided at the detector, control panel and remote annunciator. The balance of the system installation shall comply with NFPA 720 and with the Uniform Construction Code. Carbon monoxide and fire alarms may be incorporated into a common monitored system. 5. Carbon monoxide alarms shall be manufactured, listed and labeled in accordance with UL 2034 and shall be installed and maintained in accordance with the requirements of this section and the edition of NFPA 720 currently referenced in this chapter, as applicable. Carbon monoxide alarms may be battery operated, hard wired or of the plug-in type. Expired alarms shall be immediately replaced. 6. Carbon monoxide detection systems shall comply with the edition of NFPA 720 currently referenced in this chapter. Carbon monoxide detectors shall be listed in accordance with UL 2075. |  | Carbon Monoxide Detectors shall be installed>
FPVIO-24-1726069851 | FALSE | Sportsmed Pt LLC | 21 S.Spring Valley Road | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723820188 | FALSE | David Gregory School | David Gregory School | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723745209 | FALSE | Psychogenics | Psychogenics | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | outside of mouse room | Storage not permitted in means of egress>
FPVIO-24-1723821285 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723821267 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723825024 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. | stairs near lobby | Fire Protection system maintenance required. annual testing of fire roll down door required>
FPVIO-24-1725558159 | FALSE | Lowe's Home Centers |  | 901.4.1 | All fire protection systems shall be maintained in an operative condition at all times. An owner or occupant shall not reduce the effectiveness of the protection so required. This requirement shall not prohibit the owner or occupant from temporarily reducing or discontinuing the protection where necessary to make tests, repairs, alterations or additions. The fire official shall be notified before disconnection or interruption of protection and when tests, repairs, alterations or additions are started and upon completion of such work. The fire official shall be advised of the extent of and reason for such work, and the restoration of the protection shall be diligently pursued. |  | Fire Protection system maintenance required Sprinkler report from 8-29-2024 has deficiency. must be addressed and report forwarded to Fire prevention with repairs.>
FPVIO-24-1725634326 | FALSE | Ridge Ranch School | Ridge Ranch School | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. | refer to inspection report | Fire alarm maintenance required./RN>
FPVIO-24-1723826752 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | 400 level exit door | Exit/ Direction Signs shall be maintained>
FPVIO-24-1723826004 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | near room 401 | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1725643088 | FALSE | Fifty58 | Fifty58 | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | both stairwells. check and repair all lights | Emergency egress lighting shall be maintained>
FPVIO-24-1723825786 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | lower level by rm 319 | Emergency egress lighting shall be maintained>
FPVIO-24-1723825736 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | lower level by rm 319 | Exit/ Direction Signs shall be maintained>
FPVIO-24-1725643136 | FALSE | Fifty58 | Fifty58 | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | all roof doorways | Exit/ Direction Signs shall be maintained>
FPVIO-24-1723825828 | FALSE | Yavneh Academy | 155 N. Farview Avenue | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | stairwell by rm 319 | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1723744453 | FALSE | Psychogenics | Psychogenics | 605.3.1 | Doors into electrical control panel rooms shall be marked with a plainly visible and legible sign stating ELECTRICAL ROOM or similar approved wording. The disconnecting means for each service, feeder or branch circuit originating on a switchboard or panel-board shall be legibly and durably marked to indicate its purpose unless such purpose is clearly evident. | by 500 office areas | Electrical Room shall be clearly identified>
FPVIO-24-1723736017 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 906.9 | The installation of portable fire extinguishers shall be in accordance with Sections 906.9.1 through 906.9.3. | Priest room in church | Fire Extinguisher shall be properly mounted>
FPVIO-24-1723735406 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 605.3.1 | Doors into electrical control panel rooms shall be marked with a plainly visible and legible sign stating ELECTRICAL ROOM or similar approved wording. The disconnecting means for each service, feeder or branch circuit originating on a switchboard or panel-board shall be legibly and durably marked to indicate its purpose unless such purpose is clearly evident. | Electrical panels throughout the building | All circuits shall be properly identified in electrical panel.>
FPVIO-24-1726251821 | FALSE | TD Bank | TD Bank | 605.1 | Identified electrical hazards shall be abated. Identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the electrical subcode of the Uniform Construction Code Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used. All electrical wiring, devices, appliances and other equipment shall be maintained in accordance with the provisions of the electrical subcode of the New Jersey Uniform Construction Code and this sub-chapter. | Private room | Electrical Hazard shall be abated>
FPVIO-24-1726252048 | FALSE | Tesla Electric Cars | 530 Route 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. | Parking lot and access road | Fire Lanes and fire apparatus access roads shall not be obstructed. 25 vehicles were improperly parked through out the property/RN>
FPVIO-24-1726252638 | FALSE | 277 Forest LLC (Common Area) | 277 Forest LLC (Common Area) | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | outside of suite 101 | Storage not permitted in means of egress>
FPVIO-24-1726500726 | FALSE | Audiology & Hearing | Audiology & Hearing | 241-9, A | The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt.The owner of all businesses, occupancies, buildings, structures or premises required to be inspected under the requirements of the Uniform Fire Code shall register annually with the Fire Prevention Bureau upon forms provided by the Fire Official. It shall be a violation of this chapter for an owner to fail to return such forms to the Fire Prevention Bureau within 30 days of receipt. |  | Failure to obtain annual fire prevention registration./RN>
FPVIO-24-1726253319 | FALSE | 277 Forest LLC (Common Area) | 277 Forest LLC (Common Area) | 703.2 | Opening protectives shall be maintained in an operative condition in accordance with NFPA 80. Where allowed by the fire code official, the application of field-applied labels associated with the maintenance of opening protectives shall follow the requirements of the approved third-party certification organization accredited for listing the opening protective. Fire doors and smoke barrier doors shall not be blocked or obstructed, or otherwise made inoperable. Door stops, wedges and other unapproved hold-open devices shall be prohibited. Fusible links shall be replaced promptly whenever fused or damaged. Fire door assemblies shall not be modified. | by suite 120 1Fl stairway entrance | Fire Doors shall not be blocked open or obstructed.>
FPVIO-24-1726253988 | FALSE | HMH - Endocrinology | HMH - Endocrinology | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | server room | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1726247577 | FALSE | EPIC | EPIC | 605.3.1 | Doors into electrical control panel rooms shall be marked with a plainly visible and legible sign stating ELECTRICAL ROOM or similar approved wording. The disconnecting means for each service, feeder or branch circuit originating on a switchboard or panel-board shall be legibly and durably marked to indicate its purpose unless such purpose is clearly evident. | Ground floor | Electrical Room shall be clearly identified>
FPVIO-24-1723736303 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 404.2.1 | Fire evacuation plans shall include the following: /RN1. Emergency egress or escape routes and whether evacuation of the building is to be complete by selected floors or areas only or with a defend-in-place response. /RN2. Procedures for employees who must remain to operate critical equipment before evacuating. /RN3. Procedures for the use of elevators to evacuate the building where occupant evacuation elevators complying with the building subcode of the Uniform Construction Code are provided. /RN4. Procedures for assisted rescue for persons unable to use the general means of egress unassisted. /RN5. Procedures for accounting for employees and occupants after evacuation has been completed. /RN6. Identification and assignment of personnel responsible for rescue or emergency medical aid. /RNEMERGENCY PLANNING AND PREPAREDNESS /RN7. The preferred and any alternative means of notifying occupants of a fire or emergency. /RN8. The preferred and any alternative means of reporting fires and other emergencies to the fire department or designated emergency response organization. /RN9. Identification and assignment of personnel who can be contacted for further information or explanation of duties under the plan. /RN10. A description of the emergency voice/alarm communication system alert tone and preprogrammed voice messages, where provided. | Room 209 | Egress Maps Required.>
FPVIO-24-1726072695 | FALSE | Damasa Perfume Level 2 R071Z Kiosk | One Garden State Plaza | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1723736417 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 404.2.1 | Fire evacuation plans shall include the following: /RN1. Emergency egress or escape routes and whether evacuation of the building is to be complete by selected floors or areas only or with a defend-in-place response. /RN2. Procedures for employees who must remain to operate critical equipment before evacuating. /RN3. Procedures for the use of elevators to evacuate the building where occupant evacuation elevators complying with the building subcode of the Uniform Construction Code are provided. /RN4. Procedures for assisted rescue for persons unable to use the general means of egress unassisted. /RN5. Procedures for accounting for employees and occupants after evacuation has been completed. /RN6. Identification and assignment of personnel responsible for rescue or emergency medical aid. /RNEMERGENCY PLANNING AND PREPAREDNESS /RN7. The preferred and any alternative means of notifying occupants of a fire or emergency. /RN8. The preferred and any alternative means of reporting fires and other emergencies to the fire department or designated emergency response organization. /RN9. Identification and assignment of personnel who can be contacted for further information or explanation of duties under the plan. /RN10. A description of the emergency voice/alarm communication system alert tone and preprogrammed voice messages, where provided. | Room 311 | Egress Maps Required.>
FPVIO-24-1723736344 | FALSE | Our Lady of the Visitation Academy | 222 Farview Avenue | 404.2.1 | Fire evacuation plans shall include the following: /RN1. Emergency egress or escape routes and whether evacuation of the building is to be complete by selected floors or areas only or with a defend-in-place response. /RN2. Procedures for employees who must remain to operate critical equipment before evacuating. /RN3. Procedures for the use of elevators to evacuate the building where occupant evacuation elevators complying with the building subcode of the Uniform Construction Code are provided. /RN4. Procedures for assisted rescue for persons unable to use the general means of egress unassisted. /RN5. Procedures for accounting for employees and occupants after evacuation has been completed. /RN6. Identification and assignment of personnel responsible for rescue or emergency medical aid. /RNEMERGENCY PLANNING AND PREPAREDNESS /RN7. The preferred and any alternative means of notifying occupants of a fire or emergency. /RN8. The preferred and any alternative means of reporting fires and other emergencies to the fire department or designated emergency response organization. /RN9. Identification and assignment of personnel who can be contacted for further information or explanation of duties under the plan. /RN10. A description of the emergency voice/alarm communication system alert tone and preprogrammed voice messages, where provided. | Room 201 | Egress Maps Required.>
FPVIO-24-1726072971 | FALSE | Mimi & Pin PK #9246 | One Garden State Plaza | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1726156081 | FALSE | Westfield Garden State Plaza Parking Structure B | Westfield Garden State Plaza Parking Structure B | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Level 3- J | Exit/ Direction Signs shall be maintained>
FPVIO-24-1726241861 | FALSE | Raymour & Flanigan Furniture | 200 Route 17 | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. | Fire Alarm Room | Fire alarm maintenance required./RN>
FPVIO-24-1726072980 | FALSE | Mimi & Pin PK #9246 | One Garden State Plaza | 904.5.1 | Systems shall be inspected and tested for proper operation at six-month intervals. Tests shall include a check of the detection system, alarms and releasing devices, including manual stations and other associated equipment. Extinguishing system units shall be weighed and the required amount of agent verified. Stored pressure-type units shall be checked for the required pressure. The cartridge of cartridge-operated units shall be weighed and replaced at intervals indicated by the manufacturer. |  | Wet Chemical Suppression System inspection required (6 Months)>
FPVIO-24-1726154853 | FALSE | Westfield Garden State Plaza Parking Structure B | Westfield Garden State Plaza Parking Structure B | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Lower Level by Food court entrance | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1723835823 | FALSE | Valley Hospital Medical Arts Building | Valley Hospital Medical Arts Building | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1725026448 | FALSE | AMC Theatre | AMC Theatre | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Theatre room 3 | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1723835828 | FALSE | Valley Hospital Medical Arts Building | Valley Hospital Medical Arts Building | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-00132 | FALSE | Home Depot | Home Depot | 5:70-2.16(a) | If, upon an inspection, the enforcing agency discovers a violation of the Act that constitutes an imminent hazard as defined in (b) below, the enforcing agency shall issue and cause to be served on the owner of the premises, or on the violator, a written order directing that the premises be vacated, closed, or removed forthwith or that the violation be corrected within a period not to exceed 24 hours. The order shall state the nature of the violation and the date and hour by which the premises shall be vacated, closed or removed or the violation shall be abated. | Property- Fire Sprinkler Supply Line | Inadequacy of Fire Protection System>
FPVIO-24-1725026503 | FALSE | AMC Theatre | AMC Theatre | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Throughout film rooms | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1725028888 | FALSE | Forever 21 #1200 Level 1 & 2 B11 | Forever 21 #1200 Level 1 & 2 B11 | 1031.5 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | Stockroom | Means of egress shall not be obstructed.>
FPVIO-24-1725028954 | FALSE | Forever 21 #1200 Level 1 & 2 B11 | Forever 21 #1200 Level 1 & 2 B11 | 907.8.1 | Where required for compliance with the provisions of this code, devices, equipment, systems, conditions, arrangements, levels of protection or other features shall thereafter be continuously maintained in accordance with applicable NFPA requirements or as directed by the fire code official. | Fire alarm room | Fire alarm maintenance required./RN Alarm panel showing supervisory trouble >
FPVIO-24-1725027506 | FALSE | AMC Theatre | AMC Theatre | 315.3.1 | Storage shall be maintained 2 feet (610 mm) or more below the ceiling in nonsprinklered areas of buildings or in accordance with NFPA 25 with a minimum of not less than 18 inches (457 mm) below sprinkler head deflectors in sprinklered areas of buildings. | Main storage | Storage shall not be within 18 Inches of ceiling in sprinklered building./RN>
FPVIO-24-1725028424 | FALSE | Forever 21 #1200 Level 1 & 2 B11 | Forever 21 #1200 Level 1 & 2 B11 | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | Throughout the store | Emergency egress lighting shall be maintained>
FPVIO-24-1724869685 | FALSE | Advanced Data | 15 Prospect Street | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | back emergency stairwell | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1724858799 | FALSE | Paramus Fire Company # 1 | 19 Firehouse Lane | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-00118 | FALSE | Yeshivat Noam | Yeshivat Noam | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724788729 | FALSE | Borough of Paramus- Borough Hall | 1 Jockish Square | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | emergency light 23, 2nd floor- outside IT | Emergency egress lighting shall be maintained>
FPVIO-24-1724789873 | FALSE | Borough of Paramus- Borough Hall | 1 Jockish Square | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | south stairwell- Emergency light 1 | Emergency egress lighting shall be maintained>
FPVIO-24-1724866739 | FALSE | Crate & Barrel | Crate & Barrel | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724867704 | FALSE | Crate & Barrel | Crate & Barrel | 1031.1.1 | Combustible or flammable material shall not be placed, stored or kept in any portion of an exit, elevator car or hoist way, or at the bottom of a stairway, fire escape or other means of escape, unless such space is enclosed and protected as required by the construction code in effect at the time of first occupancy. Such storage shall be located so the presence or burning of the materials will not obstruct or render hazardous the means of egress. | emergency stairwell | Storage not permitted in means of egress>
FPVIO-24-1724867766 | FALSE | Crate & Barrel | Crate & Barrel | 605.3 | A working space of not less than 30 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided in front of electrical service equipment. Where the electrical service equipment is wider than 30 inches (762 mm), the working space shall be not less than the width of the equipment. Storage of materials shall not be located within the designated working space. /RNExceptions: /RN1. Where other dimensions are required or allowed by the electrical subcode of the Uniform Construction Code. /RN2. Access openings into attics or under-floor areas which provide a minimum clear opening of 22 inches (559 mm) by 30 inches (762 mm). | 2nd floor stockroom | Storage not permitted within 36 Inches of electrical service equipment.>
FPVIO-24-1724866753 | FALSE | Crate & Barrel | Crate & Barrel | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1724866791 | FALSE | Crate & Barrel | Crate & Barrel | 903.5 | Sprinkler systems shall be tested and maintained in accordance with Section 901. | THROUGHOUT SALES FLOOR 1st and 2nd floor | Missing sprinkler concealer caps shall be replaced./RN>
FPVIO-24-1725031802 | FALSE | Stew Leonard's | Stew Leonard's | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1725381809 | FALSE | Wetzel's Pretzel Level 1 | Wetzel's Pretzel Level 1 | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. | Kiosk | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1725382408 | FALSE | Mariann's School of Dance, Inc | Mariann's School of Dance, Inc | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | above room 4 | Exit/ Direction Signs shall be maintained>
FPVIO-24-1723835036 | FALSE | Western Termite & Pest Control | Western Termite & Pest Control | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1725382472 | FALSE | Mariann's School of Dance, Inc | Mariann's School of Dance, Inc | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. /RNExceptions: /RN1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. /RN2. Thirty-day inspections shall not be required and maintenance shall be allowed to be once every 3 years for dry-chemical or halogenated agent portable fire extinguishers that are supervised by a listed and approved electronic monitoring device, provided that all of the following conditions are met: /RN2.1. Electronic monitoring shall confirm that extinguishers are properly positioned, properly charged and unobstructed. /RN2.2. Loss of power or circuit continuity to the electronic monitoring device shall initiate a trouble signal. /RN2.3. The extinguishers shall be installed inside of a building or cabinet in a noncorrosive environment. /RN2.4. Electronic monitoring devices and supervisory circuits shall be tested every 3 years when extinguisher maintenance is performed. /RN2.5. A written log of required hydrostatic test dates for extinguishers shall be maintained by the owner to verify that hydrostatic tests are conducted at the frequency required by NFPA 10. /RN3. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations. |  | Fire Extinguisher overdue for maintenance/inspection.>
FPVIO-24-1723830389 | FALSE | Ridge Ranch School | Ridge Ranch School | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1723828280 | FALSE | Ben Porat Yosef | 243 Frisch Court | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | outside room 209 | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1725381357 | FALSE | Wired Products LLC | Wired Products LLC | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | shipping hallway | Emergency egress lighting shall be maintained>
FPVIO-24-1725032995 | FALSE | Stew Leonard's | Stew Leonard's | 1013.1 | All means of egress shall be indicated with approved “Exit” signs where required by the construction code in effect at the time of first occupancy or N.J.A.C. 5:70-4 et seq., as applicable. All “Exit” signs shall be maintained visible, and all illuminated exit signs shall be illuminated at all times the structure is occupied. Supplemental internally illuminated directional signs, when necessary, shall be installed in accordance with the technical requirements of the Uniform Construction Code indicating the direction and way of egress. /RNExceptions: /RN1. Exit signs are not required in rooms or areas that require only one exit or exit access. /RN2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the fire code official. /RN3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3. /RN4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3. /RN5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. | Warwhouse behind seafood | Exit/ Direction Signs shall be maintained>
FPVIO-24-1725033095 | FALSE | Stew Leonard's | Stew Leonard's | 5303.5.3 | Compressed gas containers, cylinders and tanks shall be secured to prevent falling caused by contact, vibration or seismic activity. Securing of compressed gas containers, cylinders and tanks shall be by one of the following methods: /RN/RN1. Securing containers, cylinders and tanks to a fixed object with one or more restraints. /RN/RN2. Securing containers, cylinders and tanks on a cart or other mobile device designed for the movement of compressed gas containers, cylinders or tanks. /RN/RN3. Nesting of compressed gas containers, cylinders and tanks at container filling or servicing facilities or in sellers’ warehouses not accessible to the public. Nesting shall be allowed provided the nested containers, cylinders or tanks, if dislodged, do not obstruct the required means of egress. /RN/RN4. Securing of compressed gas containers, cylinders and tanks to or within a rack, framework, cabinet or similar assembly designed for such use. /RN/RNException: Compressed gas containers, cylinders and tanks in the process of examination, filling, transport or servicing. | Receiving area | Compressed gas cylinders/containers shall be secured>
FPVIO-24-1725031815 | FALSE | Stew Leonard's | Stew Leonard's | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire sprinkler inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1725032308 | FALSE | Stew Leonard's | Stew Leonard's | 703.1 | The required fire-resistance rating of fire-resistance-rated construction, including, but not limited to, walls, firestops, shaft enclosures, partitions, smoke barriers, floors, fire-resistive coatings and sprayed fire-resistant materials applied to structural members and fire-resistant joint systems, shall be maintained. Such elements shall be visually inspected by the owner annually and properly repaired, restored or replaced where damaged, altered, breached or penetrated. Records of inspections and repairs shall be maintained. Where concealed, such elements shall not be required to be visually inspected by the owner unless the concealed space is accessible by the removal or movement of a panel, access door, ceiling tile or similar movable entry to the space. Openings made therein for the passage of pipes, electrical conduit, wires, ducts, air transfer openings and holes made for any reason shall be protected with approved methods capable of resisting the passage of smoke and fire. Openings through fire-resistance-rated assemblies shall be protected by self- or automatic-closing doors of approved construction meeting the fire protection requirements for the assembly. | Upstairs hallway | Holes in fire rated walls/ceiling shall be repaired/RN>
FPVIO-24-1725033235 | FALSE | Stew Leonard's | Stew Leonard's | 609.3.3.2 | If during the inspection it is found that hoods, grease-removal devices, fans, ducts or other appurtenances have an accumulation of grease, such components shall be cleaned in accordance with ANSI/IKECA C 10. | Kitchen | Grease accumulations of kitchen suppression nozzles shall be removed.>
FPVIO-24-1725381232 | FALSE | Wired Products LLC | Wired Products LLC | 315.3.1 | Storage shall be maintained 2 feet (610 mm) or more below the ceiling in nonsprinklered areas of buildings or in accordance with NFPA 25 with a minimum of not less than 18 inches (457 mm) below sprinkler head deflectors in sprinklered areas of buildings. | router cage storage | Storage shall not be within 18 Inches of ceiling in sprinklered building./RN>
FPVIO-24-1723835157 | FALSE | Western Termite & Pest Control | Western Termite & Pest Control | 901.6.2 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years and forwarded to the fire official within five business days of the inspection. All inspection reports shall list deficiencies based on the edition of the referenced standard in effect at the time of installation, with nonrequired recommendations listed separately. |  | Annual fire alarm inspection report shall be emailed to Fire Prevention Bureau>
FPVIO-24-1725378146 | FALSE | Physician Specialists of Northern Jersey | 1 Sears Drive | 1010.4 | Locks or fasteners shall not be installed on egress doors, except in accordance with the following conditions: /RN1. In mental, penal or other institutions where the security of inmates is necessary, in which case properly trained supervisory personnel shall be continuously on duty and approved provisions shall be made to remove occupants safely in case of a fire or other emergencies. /RN2. In problem security areas, special-purpose door alarms or locking devices shall be approved prior to installation. Manually operated edge or surface-molded flush bolts shall be prohibited. /RN3. Where the door hardware is in compliance with the Uniform Construction Code. | Main entrance | Unapproved locks shall be removed./RN Maglock must be inspected and approved by Fire Prevention>
FPVIO-24-1725381092 | FALSE | Wired Products LLC | Wired Products LLC | 1008.2 | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied. /RNExceptions: /RN1. Occupancies in Group U. /RN2. Aisle accessways in Group A. /RN3. Dwelling units and sleeping units. | cubicle area | Emergency egress lighting shall be maintained>
FPVIO-25-00073 | FALSE | Skechers #2701 | 730 Bergen Town Center | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00074 | FALSE | Skechers #2701 | 730 Bergen Town Center | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00072 | FALSE | MP Care Inc | 80 E. Route 4 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00070 | FALSE | Midland Deli & Grill | 369 E. Midland Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00071 | FALSE | MP Care Inc | 80 E. Route 4 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00078 | FALSE | Anthony Sapienza Family Dentist | 106 E. Ridgewood Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00079 | FALSE | Dunkin Dounuts/Baskin Robbin's | 494 Route 17 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00077 | FALSE | Anthony Sapienza Family Dentist | 106 E. Ridgewood Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00075 | FALSE | Alliance Medibilling, LLC | 37 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00076 | FALSE | Alliance Medibilling, LLC | 37 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00064 | FALSE | Loan Depot | 12 Route 17 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Prevention 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00065 | FALSE | Mattress Warehouse | 145 E. Route 4 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Prevention 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00063 | FALSE | Loan Depot | 12 Route 17 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Prevention 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00061 | FALSE | JFC Funding | 80 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Prevention 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00062 | FALSE | JFC Funding | 80 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Prevention 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00068 | FALSE | Midland Deli & Grill | 369 E. Midland Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00069 | FALSE | Midland Deli & Grill | 369 E. Midland Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00067 | FALSE | Midland Deli & Grill | 369 E. Midland Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00066 | FALSE | Mattress Warehouse | 145 E. Route 4 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Prevention 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00080 | FALSE | Dunkin Dounuts/Baskin Robbin's | 494 Route 17 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00084 | FALSE | Goldman Sachs Personal Financial Management | 115 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00085 | FALSE | Mattress Firm | 451 Route 17 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00083 | FALSE | Goldman Sachs Personal Financial Management | 115 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00081 | FALSE | Excel Entertainment | 106 E. Ridgewood Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00082 | FALSE | Excel Entertainment | 106 E. Ridgewood Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00086 | FALSE | Mattress Firm | 451 Route 17 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00033 | FALSE | Prestige Medical & Rehab | 80 E. Ridgewood Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00034 | FALSE | Prestige Medical & Rehab | 80 E. Ridgewood Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00032 | FALSE | Merrill Lynch - Suite 200 | 115 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00030 | FALSE | DiMaria & DiMaria Attorneys at Law | 36 Farview Terrace | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00031 | FALSE | Merrill Lynch - Suite 200 | 115 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00038 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00039 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00037 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00035 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00036 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00023 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00024 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00022 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00020 | FALSE | Mercury Pest Control and Common Areas | 25 N. Farview Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00021 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2021 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00028 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00029 | FALSE | DiMaria & DiMaria Attorneys at Law | 36 Farview Terrace | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00027 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00025 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2021 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00026 | FALSE | Ralphy's Pizza Restaurant | 440 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00040 | FALSE | Silicom | 6 Forest Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00058 | FALSE | Focus Partners & Dr. Raymond Dimetrovsky | 22 Madison Avenue | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00059 | FALSE | Express Factory | 540 Bergen Town Center | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Prevention 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00057 | FALSE | Focus Partners & Dr. Raymond Dimetrovsky | 22 Madison Avenue | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00055 | FALSE | Door Design Lab | 484 Route 17 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00056 | FALSE | Door Design Lab | 484 Route 17 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00060 | FALSE | Express Factory | 540 Bergen Town Center | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Prevention 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00044 | FALSE | NJ Pain & Rehabilitation Center | 30 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2024 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00045 | FALSE | NJ Pain & Rehabilitation Center | 37 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00043 | FALSE | NJ Pain & Rehabilitation Center | 30 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00041 | FALSE | NJ Pain & Rehabilitation Center | 30 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00042 | FALSE | NJ Pain & Rehabilitation Center | 30 W. Century Road | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2024 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00049 | FALSE | Advanced Surgical Solutions (Suite 102) | 140 N. Route 17 | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2023 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00050 | FALSE | Advanced Surgical Solutions (Suite 102) | 140 N. Route 17 | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2023 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00048 | FALSE | Mutual of Omaha | 40 Eisenhower Drive | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00046 | FALSE | NJ Pain & Rehabilitation Center | 37 W. Century Road | 241-9 F (1) | The penalty for failure to register annually with the Fire Prevention Bureau, within 30 calendar days after having been ordered to do so, shall result in a penalty amount equal to double the applicable registration fee. | Fire Registration 2022 | Failure to obtain annual fire prevention registration.>
FPVIO-25-00047 | FALSE | Mutual of Omaha | 40 Eisenhower Drive | 241-9 F (2) | The penalty for failure to pay the registration fee, within 30 calendar days after having been ordered to do so, shall be an amount equal to double the unpaid fee. | Fire Registration 2022 | Failure to pay the registration fee, within 30 calendar days.>
FPVIO-25-00100 | FALSE | Elite Spin & Sports Care Of Paramus | Elite Spin & Sports Care Of Paramus | 906.2 | Portable fire extinguishers shall be selected, installed and maintained in accordance with this section and NFPA 10. Exceptions: 1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. | Throughout | Fire extinguisher overdue for maintenance/inspection/RN>
FPVIO-25-1737732151 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737732022 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737732122 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731818 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731867 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731798 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731740 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731773 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731973 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731999 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731944 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731889 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1737731925 | FALSE | 530 ROUTE 17 | 530 ROUTE 17 | 503.4 | Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times. |  | Fire lane shall not be obstructed>
FPVIO-25-1738264127 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 906.6 | Portable fire extinguishers shall not be obstructed or obscured from view. In rooms or areas in which visual obstruction cannot be completely avoided, means shall be provided to indicate the locations of extinguishers. | showroom North East exit | Fire extinguisher access shall not be obstructed/RN>
FPVIO-25-1738264166 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 1031.3 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | showroom Northeast exit | Means of egress shall not be obstructed>
FPVIO-25-1738264083 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 604.4 | Multiplug adapters, such as cube adapters, unfused plug strips or any other device not complying with the Electrical Subcode of the Uniform Construction Code shall be prohibited. | Showroom north East exit | Multi-plug adapters prohibied>
FPVIO-25-1738263813 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 1031.3 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. |  | Means of egress shall not be obstructed>
FPVIO-25-1738263883 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 906.6 | Portable fire extinguishers shall not be obstructed or obscured from view. In rooms or areas in which visual obstruction cannot be completely avoided, means shall be provided to indicate the locations of extinguishers. |  | Fire extinguisher access shall not be obstructed/RN>
FPVIO-25-1738264486 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 315.3.3 | Combustible material shall not be stored in boiler rooms, mechanical rooms, electrical equipment rooms or in fire command centers as specified in Section 508.1.5. | Electrical Room | Storage not permitted in utility rooms>
FPVIO-25-1738264251 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 315.3.3 | Combustible material shall not be stored in boiler rooms, mechanical rooms, electrical equipment rooms or in fire command centers as specified in Section 508.1.5. | sprinkler room | Storage not permitted in utility rooms>
FPVIO-25-1738264355 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 1031.3 | A means of egress shall be free from obstructions that would prevent its use, including the accumulation of snow and ice. | both north exits from clearance area | Means of egress shall not be obstructed>
FPVIO-25-1738263597 | FALSE | Paramus Furniture Liquidators | Paramus Furniture Liquidators | 901.6.3 | Records of all system inspections, tests and maintenance required by the referenced standards shall be maintained on the premises for a minimum of three years. Every permitted and certified contractor shall provide a copy of the completed report to both t |  | Annual Fire Alarm inspection report shall be emailed to Fire Prevention Bureau/RN>