## ViolationRpt.xls
Juris | EnteredDate | Category | Action | ViolationCode | Priority | Status | StatusDate | Occupancy
HC | 10/24/2019 |  | Make repairs/replacement as needed to all carbon monoxide detection systems/devices | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 11/21/2019 |  | Have current systems tested | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 01/29/2020 |  | Sevice carbon monoxide detection system | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/21/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 02/19/2020 | 450 Hackensack Ave,16
HC | 02/06/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 03/09/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 04/07/2020 | 21 Shafer Pl
HC | 01/28/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 02/19/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/19/2020 | 20 Mercer St
HC | 03/13/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 08/09/2020 | 390 Hackensack Ave,182A
HC | 03/11/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 04/09/2020 | 450 Hackensack Ave,6
HC | 05/12/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/18/2020 | 100 S Main St
HC | 01/09/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/19/2020 | 190 Main St,402
HC | 01/09/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 03/19/2020 | 190 Main St,402
HC | 12/24/2019 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/15/2020 | 112 Myer St
HC | 03/03/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 04/01/2020 | 115 Lawrence St
HC | 03/02/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 05/20/2020 | 28 Van Orden Pl
HC | 07/23/2019 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 06/03/2020 | 10 First St
HC | 02/10/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 06/20/2020 | 325 S River St
HC | 03/04/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 06/27/2020 | 3 University Plz,614
HC | 03/03/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 06/26/2020 | 324 Railroad Ave
HC | 02/03/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/03/2020 | 359 Main St
HC | 07/10/2019 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/15/2020 | 369 Essex St
HC | 12/20/2019 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 01/18/2020 | 297 Hudson St,1st Flr
HC | 01/09/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/15/2020 | 105 Main St,4
HC | 01/09/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 03/15/2020 | 105 Main St,4
HC | 01/22/2020 | Extinguishers | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Mount at 42". | N.J.A.C. 5:70-3, 906.7 |  | Unabated | 02/20/2020 | 154 Lodi St
HC | 02/19/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/11/2020 | 236 Main St
HC | 06/09/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 07/08/2020 | 641 Main St
HC | 06/16/2020 | Extinguishers | Fire extinguisher(s) need to be mounted in a visible location for occupant access, Extinguishers shall be immediately available for use. Locate extinguisher(s) near exit(s), mounted at 42 inches to neck with approved hardware. | N.J.A.C. 5:70-3, 906.5 |  | Unabated | 07/15/2020 | 343 S River St
HC | 06/24/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/23/2020 | 16 Marion St,2
HC | 03/10/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 04/08/2020 | 15 Emerald St,A
HC | 11/27/2019 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 12/26/2019 | 292 Main St,Building
HC | 03/06/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 04/04/2020 | 48 Orchard St
HC | 02/21/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/21/2020 | 90 W Franklin St
HC | 03/03/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 07/31/2020 | 380 W Pleasantview Ave,4
HC | 02/26/2020 | Extinguishers | Fire extinguisher(s) shall be inspected and tested in accordance with NFPA 10, Current certification expired. | N.J.A.C. 5:70-3, 906.2 |  | Unabated | 03/26/2020 | 139 Main St,BLDG
HC | 07/06/2020 | Stairs & Doors | Sliding and rolling fire doors shall be maintained, tested and inspected. |  |  | Unabated | 08/04/2020 | 138 Kansas St
HC | 01/28/2020 | Stairs & Doors | Approved self-closing devices shall be maintained, Do Not Chock Open Fire Door. |  |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 09/20/2019 | Stairs & Doors | All fire doors must close and latch, Repair or Replace fire doors. |  |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 02/06/2020 | Stairs & Doors | All fire doors must close and latch, Repair or Replace fire doors. |  |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 01/21/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 02/19/2020 | 450 Hackensack Ave,16
HC | 03/13/2020 | Emergency Lighting | Exit signs shall be illuminated at all times | N.J.A.C. 5:70-3, [BE] 1013.1 |  | Unabated | 08/03/2020 | 387 Rte 17 S
HC | 11/18/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 12/17/2019 | 1 University Plz,618
HC | 10/04/2019 | Emergency Lighting | Battery back up emergency lights required to be installed in egress path. Obtain electrical permit and have fixture(s) installed. | N.J.A.C. 5:70-4.11.(j) |  | Unabated | 11/02/2019 | 40 Broadway
HC | 09/20/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 05/22/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 06/20/2020 | 175 Lexington Ave,A
HC | 10/09/2019 | Emergency Lighting |  | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/01/2020 | 10 E Camden St
HC | 05/20/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/30/2020 | 293 Main St
HC | 03/02/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/23/2020 | 320 Hamilton Pl
HC | 11/22/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/11/2020 | 102 State St
HC | 11/04/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/23/2020 | 946 Main St,2nd Flr
HC | 02/20/2020 | Emergency Lighting | Annual emergency/exit lighting annual test is required. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/21/2020 | 86-110 Orchard St,5
HC | 03/12/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 04/10/2020 | 111 Essex St
HC | 06/24/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/23/2020 | 16 Marion St,2
HC | 02/19/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/03/2020 | 52 First St
HC | 02/19/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/03/2020 | 52 First St
HC | 02/19/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 07/03/2020 | 52 First St
HC | 07/30/2019 | Emergency Lighting | Annual emergency/exit lighting annual test is required. Submit documentation of completion of 1 hour test. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 01/28/2020 | 390 Hackensack Ave,70
HC | 02/03/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/03/2020 | 359 Main St
HC | 02/27/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/27/2020 | 171 Main St,302
HC | 10/16/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 01/28/2020 | 100 Second St
HC | 03/04/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 05/23/2020 | 2 University Plz,505
HC | 12/13/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 01/11/2020 | 390 Hackensack Ave,313
HC | 05/07/2020 | Emergency Lighting | Annual emergency/exit lighting annual test is required. Submit documentation of completion of 1 hour test. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 06/05/2020 | 70 Longview Ave
HC | 03/04/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 06/27/2020 | 3 University Plz,614
HC | 02/24/2020 | Emergency Lighting | Annual emergency/exit lighting annual test is required. Submit documentation of completion of 1 hour test. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/24/2020 | 390 Hackensack Ave,198
HC | 02/10/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 06/20/2020 | 325 S River St
HC | 01/23/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 06/26/2020 | 453 Main St
HC | 09/05/2019 | Emergency Lighting | Exit signs shall be illuminated at all times | N.J.A.C. 5:70-3, [BE] 1013.1 |  | Unabated | 06/03/2020 | 400 Hudson St,REAR
HC | 12/24/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/15/2020 | 112 Myer St
HC | 03/02/2020 | Emergency Lighting | Exit signs shall be illuminated at all times | N.J.A.C. 5:70-3, [BE] 1013.1 |  | Unabated | 05/20/2020 | 28 Van Orden Pl
HC | 03/05/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 04/03/2020 | 131 S Newman St
HC | 02/07/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 05/16/2020 | 37 Linden St
HC | 11/08/2019 | Emergency Lighting | Annual emergency/exit lighting annual test is required. Submit documentation of completion of 1 hour test. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/18/2020 | 219 Essex St
HC | 12/13/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 01/11/2020 | 1 University Plz,516
HC | 01/09/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 02/29/2020 | 24 Bergen St,1st Flr
HC | 11/22/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/05/2020 | 32 Anderson St
HC | 09/27/2019 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 11/14/2019 | Emergency Lighting | Annual emergency/exit lighting annual test is required. Submit documentation of completion of 1 hour test. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 12/13/2019 | 129 Johnson Ave
HC | 01/09/2020 | Emergency Lighting | Battery back up emergency lights required to be installed in egress path. Obtain electrical permit and have fixture(s) installed. | N.J.A.C. 5:70-4.11.(j) |  | Unabated | 03/19/2020 | 190 Main St,402
HC | 01/09/2020 | Emergency Lighting | Repair exit/emergency light fixture to illuminate when test button is pressed. | N.J.A.C. 5:70-3, 604.4.1.1 |  | Unabated | 03/19/2020 | 190 Main St,402
HC | 12/23/2019 | Compressed Gases | Compressed gas containers, cylinders, tanks and systems that could be exposed to physical damage from vehicles shall be protected by guard posts. Install same. | N.J.A.C. 5:70-3, 5303.5.2 |  | Unabated | 01/21/2020 | 30 Prospect Ave,6
HC | 12/23/2019 | Compressed Gases | Compressed gas cylinders must be secured, restrain with chain to wall or enclose in cage or vented cabinet. | N.J.A.C. 5:70-3, 5303.5.3 |  | Unabated | 01/21/2020 | 30 Prospect Ave,6
HC | 11/26/2019 | Compressed Gases | CO2 Detection systems shall be tested and certified at least annually. Forward results of last annual test. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 5003.2.9.1 |  | Unabated | 06/19/2020 | 450 Hackensack Ave,8
HC | 11/18/2019 | Compressed Gases | Compressed gas cylinders must be secured, restrain with chain to wall or enclose in cage or vented cabinet. | N.J.A.C. 5:70-3, 5303.5.3 |  | Unabated | 05/29/2020 | 701 Main St,1ST FLR
HC | 02/19/2020 | Compressed Gases | Compressed gas cylinders must be secured, restrain with chain to wall or enclose in cage or vented cabinet. | N.J.A.C. 5:70-3, 5303.5.3 |  | Unabated | 07/03/2020 | 52 First St
HC | 12/03/2019 | Compressed Gases | Compressed gas cylinders must be secured, restrain with chain to wall or enclose in cage or vented cabinet. | N.J.A.C. 5:70-3, 5303.5.3 |  | Unabated | 01/01/2020 | 353 Railroad Ave
HC | 06/01/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/19/2020 | 87 Anderson St
HC | 11/27/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 12/26/2019 | 292 Main St,Building
HC | 11/27/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 12/26/2019 | 540 Hudson St,Building
HC | 02/11/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/11/2020 | 920 Main St,Building
HC | 02/21/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/21/2020 | 90 W Franklin St
HC | 02/18/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/31/2020 | 318 W Pleasantview Ave
HC | 03/03/2020 | Alarm System | Carbon Monoxide detectors shall be maintained as per NFPA 720 and the manufacturers instructions. Repair/replace defective detector or replace missing detector. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/31/2020 | 380 W Pleasantview Ave,4
HC | 07/08/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 08/06/2020 | 479 Main St
HC | 06/29/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 07/28/2020 | 144 Hudson St
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 30 Arcadia Rd
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 10 Arcadia Rd
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 40 Arcadia Rd
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 20 Arcadia Rd
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 34 Arcadia Rd
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 6 Cambridge Ter
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 2 Cambridge Ter
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 7 Cambridge Ter
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 16 Cambridge Ter
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 445 Thompson St
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 440 Essex St
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 26 Cambridge Ter
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 27 Cambridge Ter
HC | 02/05/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/13/2020 | 314 Main St
HC | 02/19/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/01/2020 | 248 Main St,1st Flr
HC | 10/09/2019 | Alarm System |  | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 04/28/2020 | 316 Prospect Ave
HC | 07/31/2019 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/07/2020 | 235 Main St,Building
HC | 03/12/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 04/10/2020 | 111 Essex St
HC | 02/25/2020 | Alarm System | As of 01/01/2019, all battery operated smoke alarms in 1 and 2 family homes shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 06/25/2020 | 173 High St
HC | 05/12/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/19/2020 | 240 Main St
HC | 01/30/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 02/28/2020 | 150 Kotte Pl
HC | 02/03/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 03/03/2020 | 483 Main St
HC | 01/22/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 02/20/2020 | 154 Lodi St
HC | 04/14/2020 | Alarm System | Repair Red/Blue light over Master Fire Box | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/17/2020 | 41 Rte 4 E,F
HC | 07/23/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/03/2020 | 10 First St
HC | 09/05/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/03/2020 | 400 Hudson St,REAR
HC | 04/09/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/04/2020 | 83 Summit Ave,1
HC | 11/26/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 06/19/2020 | 450 Hackensack Ave,8
HC | 02/10/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/20/2020 | 325 S River St
HC | 01/29/2020 | Alarm System | As of 01/01/2019, all battery operated smoke alarms in R-3 uses shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 06/19/2020 | 84 S State St,2nd Flr
HC | 01/29/2020 | Alarm System | As of 01/01/2019, all battery operated smoke alarms in R-3 uses shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 06/19/2020 | 84 S State St,2nd Flr
HC | 01/23/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/26/2020 | 453 Main St
HC | 02/24/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/24/2020 | 390 Hackensack Ave,198
HC | 03/03/2020 | Alarm System | Replace missing Carbon Monoxide detector. | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/26/2020 | 324 Railroad Ave
HC | 03/11/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/27/2020 | 282 Hudson St,2
HC | 04/29/2020 | Alarm System | Repair Red/Blue light over Master Fire Box | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/27/2020 | 70 Longview Ave
HC | 05/07/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 06/05/2020 | 70 Longview Ave
HC | 07/25/2019 | Alarm System | Maintenance of safeguards. Reduction of protection prohibited. Any installed level protection shall be continuously maintained. | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 11/04/2019 | 343 S River St
HC | 08/13/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/01/2020 | 27 E Kennedy St
HC | 04/06/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 05/25/2020 | 11 E Passaic St
HC | 02/26/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 06/26/2020 | 159 Main St
HC | 02/03/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 03/03/2020 | 299 Main St
HC | 12/11/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 01/09/2020 | 71 Summit Ave,2nd Flr
HC | 11/25/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/10/2020 | 149 Hudson St,L/L
HC | 02/03/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 03/03/2020 | 359 Main St
HC | 01/17/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/15/2020 | 57 Grove St
HC | 01/17/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/15/2020 | 57 Grove St
HC | 01/17/2020 | Alarm System | Carbon Monoxide detectors shall be maintained as per NFPA 720 and the manufacturers instructions. Repair/replace defective detector or replace missing detector. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 03/15/2020 | 57 Grove St
HC | 12/20/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 01/18/2020 | 297 Hudson St,1st Flr
HC | 01/17/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/15/2020 | 61 Grove St
HC | 01/17/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/15/2020 | 61 Grove St
HC | 01/17/2020 | Alarm System | Carbon Monoxide detectors shall be maintained as per NFPA 720 and the manufacturers instructions. Repair/replace defective detector or replace missing detector. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 03/15/2020 | 61 Grove St
HC | 11/08/2019 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/18/2020 | 219 Essex St
HC | 12/10/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 01/08/2020 | 26 Anderson St
HC | 09/27/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/19/2020 | 450 Hackensack Ave,7
HC | 02/07/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 05/16/2020 | 37 Linden St
HC | 02/19/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 05/14/2020 | 234 Main St
HC | 03/02/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 05/20/2020 | 28 Van Orden Pl
HC | 03/05/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 04/03/2020 | 131 S Newman St
HC | 03/05/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 04/03/2020 | 131 S Newman St
HC | 09/27/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 07/19/2019 | Alarm System | Reinstate Central Station Monitoring, forward certificate of monitoring to Fire Prevention, HFDFP@Hackensack.org | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 08/27/2019 | 294 Main St
HC | 08/21/2019 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 10/22/2019 | 25 Prospect Ave,1st Flr
HC | 08/05/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 10/15/2019 | 159 Union St,A
HC | 02/04/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/03/2020 | 59 Newman St,2nd Flr
HC | 02/04/2020 | Alarm System | Fire Watch Ordered. Building rep to maintain fire watch in areas where alarm/sprinkler is impaired. Fax log with entries every 30 min to FD at 201-646-7594. Watch is only terminated with permission of the Fire Official. | N.J.A.C. 5:70-3, 901.7 |  | Unabated | 03/03/2020 | 59 Newman St,2nd Flr
HC | 11/14/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 12/13/2019 | 129 Johnson Ave
HC | 08/22/2019 | Alarm System | Reinstate Central Station Monitoring, forward certificate of monitoring to Fire Prevention, HFDFP@Hackensack.org | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 02/17/2020 | 30 Fair St
HC | 01/29/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 02/27/2020 | 77 Lawrence St
HC | 03/10/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 04/08/2020 | 170 Sussex St,Office
HC | 03/11/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 04/09/2020 | 450 Hackensack Ave,6
HC | 04/14/2020 | Alarm System | Reinstate Central Station Monitoring, forward certificate of monitoring to Fire Prevention, HFDFP@Hackensack.org | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/28/2020 | 141 English St
HC | 05/26/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/28/2020 | 268 Kipp St
HC | 07/02/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/17/2020 | 5 Atlantic St,1
HC | 05/05/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 06/03/2020 | 360 Union St
HC | 02/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/23/2020 | 17 Cambridge Ter
HC | 03/04/2020 | Alarm System | As of 01/01/2019, all battery operated smoke alarms in 1 and 2 family homes shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 07/23/2020 | 247 Passaic St
HC | 07/16/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 08/01/2020 | 178 Green St,A
HC | 03/13/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 08/09/2020 | 390 Hackensack Ave,182A
HC | 05/22/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/25/2020 | 505 S River St
HC | 05/20/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/30/2020 | 293 Main St
HC | 11/01/2019 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 11/21/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 06/08/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/07/2020 | 450 Hackensack Ave,1
HC | 06/01/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/29/2020 | 20 Mercer St
HC | 02/19/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/19/2020 | 20 Mercer St
HC | 12/11/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 07/30/2020 | 30 Prospect Ave,11
HC | 01/28/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 06/23/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/22/2020 | 275.5 Main St
HC | 02/27/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 06/16/2020 | 382 Main St,1
HC | 06/15/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/27/2020 | 25 Hackensack Ave
HC | 02/25/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/25/2020 | 200 Main St,3
HC | 06/02/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 08/14/2020 | 300 Prospect Ave
HC | 02/06/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 12/23/2019 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 01/21/2020 | 92 Second St,Building
HC | 06/15/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/27/2020 | 107 S Summit Ave
HC | 06/15/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/27/2020 | 43 Maple Ave
HC | 01/21/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 02/19/2020 | 450 Hackensack Ave,16
HC | 06/08/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/30/2020 | 170 Hudson St
HC | 10/04/2019 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 11/02/2019 | 40 Broadway
HC | 06/09/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/27/2020 | 55 Rte 4 E
HC | 07/08/2019 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/01/2020 | 262 Hudson St
HC | 02/06/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 03/13/2020 | Alarm System | Carbon monoxide alarms shall be installed in all spaces and all adjoining spaces containing fuel burning appliances or vehicle parking. Two floors up, and down, at first HVAC vent | N.J.A.C. 5:70-4.9.(d) |  | Unabated | 08/03/2020 | 387 Rte 17 S
HC | 02/25/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 07/31/2020 | 241 Hudson St
HC | 02/25/2020 | Alarm System | Make repairs to Fire Alarm system. Forward repair report to Fire Prevention, HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/31/2020 | 241 Hudson St
HC | 03/09/2020 | Alarm System | Fire Alarm and Fire Detection systems shall be tested as per NFPA 72, submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document. | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 04/07/2020 | 16 Jefferson St,A
HC | 01/28/2020 | Building | Solar Emblem Placard required commercial building. have 6"X6" sign posted left side of the main entrance 4-6 feet high. Install above truss placard if applicable. Email the Fire Official FireOfficial@Hackensack.org for specs. | N.J.A.C. 5:70-2.21 |  | Unabated | 07/31/2020 | 260 Railroad Ave
HC | 06/23/2020 | Building | Overcrowded conditions or obstructions in aisles, passageways or other means of egress is prohibited. | N.J.A.C. 5:70-3, [A] 104.8 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 02/11/2020 | Building | Rooms containing equipment controls shall be identified. Label Door(s) leading to rooms "Fire Alarm" "Sprinkler"" "HVAC" "Electrical" "Boiler" etc as necessary | N.J.A.C. 5:70-3, 509.1 |  | Unabated | 03/11/2020 | 102 State St
HC | 05/12/2020 | Building | Rooms containing equipment controls shall be identified. Label Door(s) leading to rooms "Fire Alarm" "Sprinkler"" "HVAC" "Electrical" "Boiler" etc as necessary | N.J.A.C. 5:70-3, 509.1 |  | Unabated | 06/10/2020 | 240 Main St
HC | 06/16/2020 | Building | Fire Zone/Lane markings required. Submit plan for approval and have implimented. | N.J.A.C. 5:70-3, 503.1.1. |  | Unabated | 07/15/2020 | 343 S River St
HC | 02/25/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 06/25/2020 | 173 High St
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 12/05/2020 | 259 Berry St,2
HC | 02/07/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/29/2020 | 181-183 Grand Ave
HC | 02/20/2020 | Miscellaneous | Any dangerous condition liable to cause or contribute to the spread of fire or endanger occupants shall be prohibited. | N.J.A.C. 5:70-3, 102.1.1.1. |  | Unabated | 07/21/2020 | 86-110 Orchard St,5
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/17/2020 | 139 Van Olst St
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/17/2020 | 141 Berry St
HC | 03/10/2020 | Miscellaneous | Any dangerous condition liable to cause or contribute to the spread of fire or endanger occupants shall be prohibited. | N.J.A.C. 5:70-3, 102.1.1.1. |  | Unabated | 06/17/2020 | 390 Hackensack Ave,197
HC | 01/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 03/13/2020 | 353 Taylor Ave
HC | 09/17/2019 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 11/13/2019 | 165 Main St
HC | 12/19/2019 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 01/23/2020 | 37 E Broadway,2nd Flr
HC | 02/19/2020 | Miscellaneous | Any dangerous condition liable to cause or contribute to the spread of fire or endanger occupants shall be prohibited. | N.J.A.C. 5:70-3, 102.1.1.1. |  | Unabated | 05/14/2020 | 234 Main St
HC | 09/09/2019 | Miscellaneous | Submit building High Rise Fire Safety and Evacuation Plan for review and schedule annual fire drill with the Fire Official 201-646-3939, FireOfficial@Hackensack.org. | N.J.A.C. 5:70-3, 404.1 |  | Unabated | 05/23/2020 | 160 Overlook Ave,Building
HC | 11/08/2019 | Miscellaneous | Provide access for re-inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1.(b) |  | Unabated | 03/19/2020 | 111 Maple Ave
HC | 10/16/2019 | Miscellaneous | Remove all Fueled equipment from building. | N.J.A.C. 5:70-3, 313.1 |  | Unabated | 01/28/2020 | 100 Second St
HC | 01/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 03/13/2020 | 171 Union St
HC | 11/18/2019 | Miscellaneous | Conditions affecting the safety of fire fighters during emergency operations are prohibited. | N.J.A.C. 5:70-3, [A] 101.2.5. |  | Unabated | 12/17/2019 | 701 Main St,2ND FLR
HC | 10/04/2019 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 01/25/2020 | 853 Main St
HC | 01/02/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1(b) |  | Unabated | 05/22/2020 | 380 Main St,2nd Flr
HC | 02/05/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 03/05/2020 | 63 Green St
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/21/2020 | 114 Atlantic St
HC | 05/26/2020 | Miscellaneous | Any dangerous condition liable to cause or contribute to the spread of fire or endanger occupants shall be prohibited. | N.J.A.C. 5:70-3, 102.1.1.1. |  | Unabated | 07/28/2020 | 268 Kipp St
HC | 03/12/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/23/2020 | 262 Anderson St
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/23/2020 | 602 Main St,2nd Flr
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/23/2020 | 16 S State St
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/23/2020 | 46 Euclid Ave
HC | 03/03/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/23/2020 | 243 Second St
HC | 03/11/2020 | Miscellaneous | Provide access for re-inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. | N.J.A.C. 5:70-2.1.(b) |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 01/15/2020 | Miscellaneous | Provide access for inspection, Call 201-646-7685 to schedule inspection. Failure to do so may result in Penalties being issued. |  |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 06/08/2020 | Miscellaneous | Remove all Fueled equipment from building. | N.J.A.C. 5:70-3, 313.1 |  | Unabated | 07/30/2020 | 170 Hudson St
HC | 10/04/2019 | Miscellaneous | Any dangerous condition liable to cause or contribute to the spread of fire or endanger occupants shall be prohibited. | N.J.A.C. 5:70-3, 102.1.1.1. |  | Unabated | 11/02/2019 | 40 Broadway
HC | 06/23/2020 | Fire Resistive Rated Assembly | Holes in ceilings, walls, floors or missing ceiling tiles must be repaired/replaced. | N.J.A.C. 5:70-3, 703.1 |  | Unabated | 07/22/2020 | 275.5 Main St
HC | 05/12/2020 | Fire Resistive Rated Assembly | Curtains, draperies fabric hangings and other similar materials suspended from walls or ceilings shall be tested by an approved agency and meet flame propagation performance criteria. Forward results of last test. | N.J.A.C. 5:70-3, 807.4 |  | Unabated | 07/18/2020 | 261 Maple Hill Dr
HC | 01/17/2020 | Fire Resistive Rated Assembly | Fire doors must be maintained, Make repairs to fire/smoke doors as per NFPA 80 | N.J.A.C. 5:70-3, 703.2 |  | Unabated | 03/15/2020 | 61 Grove St
HC | 02/05/2020 | Fire Resistive Rated Assembly | Holes in ceilings, walls, floors or missing ceiling tiles must be repaired/replaced. | N.J.A.C. 5:70-3, 703.1 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 03/03/2020 | Fire Resistive Rated Assembly | Holes in ceilings, walls, floors or missing ceiling tiles must be repaired/replaced. | N.J.A.C. 5:70-3, 703.1 |  | Unabated | 07/21/2020 | 390 Hackensack Ave,131
HC | 02/25/2020 | Fire Resistive Rated Assembly | Fire doors must be maintained, Make repairs to fire/smoke doors as per NFPA 80 | N.J.A.C. 5:70-3, 703.2 |  | Unabated | 03/25/2020 | 170 Prospect Ave
HC | 01/22/2020 | Fire Resistive Rated Assembly | Holes in ceilings, walls, floors or missing ceiling tiles must be repaired/replaced. | N.J.A.C. 5:70-3, 703.1 |  | Unabated | 02/20/2020 | 154 Lodi St
HC | 05/12/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/19/2020 | 240 Main St
HC | 10/09/2019 | Sprinklers, Standpipes, Pumps |  | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 12/06/2019 | 326 Prospect Ave
HC | 04/23/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/26/2020 | 326 Prospect Ave
HC | 01/22/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 02/20/2020 | 154 Lodi St
HC | 04/14/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/13/2020 | 171 Main St,302
HC | 04/02/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/09/2020 | 86-110 Orchard St,Building
HC | 04/13/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/17/2020 | 400 Main St
HC | 04/23/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/26/2020 | 411 Passaic St
HC | 02/18/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 05/15/2020 | 325 S River St,301
HC | 04/15/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 05/14/2020 | 324 Main St
HC | 04/09/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/12/2020 | 343 S River St
HC | 10/09/2019 | Sprinklers, Standpipes, Pumps |  | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 04/28/2020 | 316 Prospect Ave
HC | 02/24/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 03/24/2020 | 316 Prospect Ave
HC | 02/25/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 03/24/2020 | 316 Prospect Ave
HC | 12/27/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/15/2020 | 120 Sussex St
HC | 02/05/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/13/2020 | 314 Main St
HC | 04/13/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/18/2020 | 436 Main St
HC | 12/05/2019 | Sprinklers, Standpipes, Pumps | Fire sprinkler systems may not be obstructed. | N.J.A.C. 5:70-3, 903.3.3 |  | Unabated | 07/03/2020 | 140 Hudson St
HC | 10/30/2019 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/19/2020 | 280 Union St
HC | 05/21/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/19/2020 | 280 Union St
HC | 05/01/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/01/2020 | 172 Johnson Ave
HC | 02/20/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/21/2020 | 86-110 Orchard St,5
HC | 07/11/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/01/2020 | 310 Lookout Ave
HC | 03/10/2020 | Sprinklers, Standpipes, Pumps | 5 Year Standpipe Flow Test Required as per NFPA 25, forward results to HFDFP@Hackensack.org | N.J.A.C. 5:70-3, 901.6.1 |  | Unabated | 07/08/2020 | 20 Atlantic St
HC | 10/16/2019 | Sprinklers, Standpipes, Pumps | Occupant-Use Fire Hose shall be tested as per NFPA 1962. Testing intervals 5 Years from date of manufacture and 3 years thereafter. | N.J.A.C. 5:70-3, 901.6.1 |  | Unabated | 01/28/2020 | 100 Second St
HC | 02/26/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 06/26/2020 | 159 Main St
HC | 04/16/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/17/2020 | 346A Main St
HC | 04/24/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 05/23/2020 | 325 S River St
HC | 04/23/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/27/2020 | 100 Prospect Ave
HC | 03/03/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 06/26/2020 | 324 Railroad Ave
HC | 08/16/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/19/2020 | 544 Main St
HC | 08/16/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/19/2020 | 554 Main St
HC | 08/16/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 03/19/2020 | 578 Main St
HC | 11/08/2019 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/18/2020 | 219 Essex St
HC | 02/18/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 05/23/2020 | 90 Prospect Ave,Building
HC | 02/07/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 05/16/2020 | 37 Linden St
HC | 09/27/2019 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 09/27/2019 | Sprinklers, Standpipes, Pumps | Have underground piping for exterior fire department connections (FDC) inspected and flushed in accordance with NFPA 25. Forward inspection report to Fire Prevention HFDFP@Hackensack.org. Notify immediately if FDC is unusable. | N.J.A.C. 5:70-3, 912.7 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 12/24/2019 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/15/2020 | 112 Myer St
HC | 12/24/2019 | Sprinklers, Standpipes, Pumps | Access to Fire Department Connections (FDCs) shall be maintained at all times. | N.J.A.C. 5:70-3, 912.4 |  | Unabated | 03/15/2020 | 112 Myer St
HC | 12/24/2019 | Sprinklers, Standpipes, Pumps | Replace missing caps on the Fire Department Connection (FDC). | N.J.A.C. 5:70-3, 901.4 |  | Unabated | 03/15/2020 | 112 Myer St
HC | 02/19/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/19/2020 | 20 Mercer St
HC | 02/19/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual standpipe system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/19/2020 | 20 Mercer St
HC | 02/19/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 03/19/2020 | 20 Mercer St
HC | 11/21/2019 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 05/20/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/30/2020 | 293 Main St
HC | 01/28/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual standpipe system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 01/28/2020 | Sprinklers, Standpipes, Pumps | Have underground piping for exterior fire department connections (FDC) inspected and flushed in accordance with NFPA 25. Forward inspection report to Fire Prevention HFDFP@Hackensack.org. Notify immediately if FDC is unusable. | N.J.A.C. 5:70-3, 912.7 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 01/28/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 11/21/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/30/2020 | 120 E Broadway
HC | 08/16/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 08/12/2020 | 586 Main St
HC | 12/30/2019 | Sprinklers, Standpipes, Pumps | Have underground piping for exterior fire department connections (FDC) inspected and flushed in accordance with NFPA 25. Forward inspection report to Fire Prevention HFDFP@Hackensack.org. Notify immediately if FDC is unusable. | N.J.A.C. 5:70-3, 912.7 |  | Unabated | 08/12/2020 | 241 Union St
HC | 03/04/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/23/2020 | 211 Mary St
HC | 11/22/2019 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/11/2020 | 102 State St
HC | 05/26/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 07/28/2020 | 268 Kipp St
HC | 04/06/2020 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/03/2020 | 360 Union St
HC | 06/01/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/18/2020 | 261 Maple Hill Dr
HC | 03/11/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 04/09/2020 | 102 State St
HC | 06/23/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 10/11/2019 | Sprinklers, Standpipes, Pumps | Make repairs to sprinkler/standpipe system, Send repair report to: HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 02/10/2020 | 140 Euclid Ave
HC | 07/11/2019 | Sprinklers, Standpipes, Pumps | Have underground piping for exterior fire department connections (FDC) inspected and flushed in accordance with NFPA 25. Forward inspection report to Fire Prevention HFDFP@Hackensack.org. Notify immediately if FDC is unusable. | N.J.A.C. 5:70-3, 912.7 |  | Unabated | 08/12/2020 | 630 Main St
HC | 04/27/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/31/2020 | 260 Railroad Ave
HC | 01/28/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 07/31/2020 | 260 Railroad Ave
HC | 06/09/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/27/2020 | 55 Rte 4 E
HC | 01/29/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual standpipe system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Sprinklers, Standpipes, Pumps | Fire pumps and transfer switches shall be inspected, tested and maintained as per NFPA 25. | N.J.A.C. 5:70-3, 913.5 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Sprinklers, Standpipes, Pumps | Visually obstructed Fire Department Connections (FDC) require signage. | N.J.A.C. 5:70-3, 912.2.2 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 05/19/2020 | Sprinklers, Standpipes, Pumps | Repair/Replace Red light over Fire Department Connection (FDC) as per IFC and city ord #166-10 | N.J.A.C. 5:70-3, [A] 104.1 |  | Unabated | 06/17/2020 | 315 State St
HC | 02/06/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual sprinkler system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Sprinklers, Standpipes, Pumps | Current NFPA annual standpipe system report requested. Submit last annual report to HFDFP@Hackensack.org Indicate which inspector is requesting the document | N.J.A.C. 5:70-3, 901.6.2 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Sprinklers, Standpipes, Pumps | Fire sprinkler systems may not be obstructed. | N.J.A.C. 5:70-3, 903.3.3 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Sprinklers, Standpipes, Pumps | Replace missing caps on the Fire Department Connection (FDC). | N.J.A.C. 5:70-3, 901.4 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 06/09/2020 | Commercial Cooking Systems | Excessive grease creating a fire hazard shall be removed and kitchen equipment cleaned, including appliances, walls, floors, etc. | N.J.A.C. 5:70-3, 102.1.1.5. |  | Unabated | 07/27/2020 | 55 Rte 4 E
HC | 06/09/2020 | Commercial Cooking Systems | Excessive grease must be removed and hood cleaned. | N.J.A.C. 5:70-3, 609.3.3.2 |  | Unabated | 07/27/2020 | 55 Rte 4 E
HC | 06/09/2020 | Commercial Cooking Systems | Have hood system cleaned and submit cleaning report to Fire Prevention HFDFP@Hackensack.org. Report shall indicate that ALL areas of the hood/duct have been cleaned. |  |  | Unabated | 07/27/2020 | 55 Rte 4 E
HC | 10/04/2019 | Commercial Cooking Systems | Cooking suppression system 6 month inspection required (wet chemical systems), submit report HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 904.5.1 |  | Unabated | 11/02/2019 | 40 Broadway
HC | 02/27/2020 | Commercial Cooking Systems | Commercial Kitchen exhaust hoods shall be maintained as per NFPA 96. | N.J.A.C. 5:70-3, [M] 609.1 |  | Unabated | 06/16/2020 | 382 Main St,1
HC | 02/27/2020 | Commercial Cooking Systems |  | N.J.A.C. 5:70-3, 609.3 |  | Unabated | 06/16/2020 | 382 Main St,1
HC | 06/15/2020 | Commercial Cooking Systems | Have hood system cleaned and submit cleaning report to Fire Prevention HFDFP@Hackensack.org. Report shall indicate that ALL areas of the hood/duct have been cleaned. |  |  | Unabated | 07/27/2020 | 43 Maple Ave
HC | 06/15/2020 | Commercial Cooking Systems | Cooking suppression system 6 month inspection required (dry chemical systems), submit report HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 904.6.1 |  | Unabated | 07/27/2020 | 43 Maple Ave
HC | 05/12/2020 | Commercial Cooking Systems | Cooking suppression system 6 month inspection required (wet chemical systems), submit report HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 904.5.1 |  | Unabated | 07/18/2020 | 100 S Main St
HC | 02/07/2020 | Commercial Cooking Systems | Cooking Operations shall be equipped with a ventilating hood, duct and automatic fire suppression system. Obtain Permits and have installed or remove cooking appliance. | N.J.A.C. 5:70-4.7.(g) |  | Unabated | 05/16/2020 | 37 Linden St
HC | 08/29/2019 | Commercial Cooking Systems | Have hood system cleaned and submit cleaning report to Fire Prevention HFDFP@Hackensack.org. Report shall indicate that ALL areas of the hood/duct have been cleaned. |  |  | Unabated | 11/04/2019 | 163 Main St,B
HC | 02/26/2020 | Commercial Cooking Systems | Cooking suppression system 6 month inspection required (wet chemical systems), submit report HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 904.5.1 |  | Unabated | 03/26/2020 | 139 Main St,BLDG
HC | 09/16/2019 | Commercial Cooking Systems | Commercial Kitchen exhaust hoods shall be maintained as per NFPA 96. | N.J.A.C. 5:70-3, [M] 609.1 |  | Unabated | 05/22/2020 | 3 University Plz,Lobby
HC | 01/29/2020 | Commercial Cooking Systems | Have hood system cleaned and submit cleaning report to Fire Prevention HFDFP@Hackensack.org. Report shall indicate that ALL areas of the hood/duct have been cleaned. |  |  | Unabated | 02/27/2020 | 390 Hackensack Ave,70
HC | 01/22/2020 | Means of Egress | Means of egress may not be obstructed, remove obstruction. | N.J.A.C. 5:70-3, 1031.1 |  | Unabated | 02/20/2020 | 154 Lodi St
HC | 02/05/2020 | Means of Egress | Fire escapes must be kept clear at all times, remove storage. | N.J.A.C. 5:70-3, 1031.1.1 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 02/26/2020 | Means of Egress | Occupancy Load sign must be posted. Obtain sign from the Fire Official. FireOfficial@Hackensack.org. | N.J.A.C. 5:70-3, [BE] 1003.4 |  | Unabated | 06/26/2020 | 159 Main St
HC | 05/19/2020 | Means of Egress | Means of egress may not be obstructed, remove obstruction. | N.J.A.C. 5:70-3, 1031.1 |  | Unabated | 06/17/2020 | 15 Conklin Pl,Sch
HC | 09/24/2019 | Means of Egress | Fire escape appears to be in a state of deterioration and in need of repair. Submit report from certified professional results from load test or documentation of repairs made with an indication that the fire escape is sound and useable. | N.J.A.C. 5:70-3, 1031.6 |  | Unabated | 01/15/2020 | 241 Main St,Building
HC | 05/12/2020 | Means of Egress | Combustible or flammable material shall not be stored, placed or kept in any portion of an exit, at the bottom of a stairway, fire escape or other means of escape. Remove all storage. | N.J.A.C. 5:70-3, 1031.1.1 |  | Unabated | 07/18/2020 | 261 Maple Hill Dr
HC | 03/13/2020 | Means of Egress | Means of egress may not be obstructed, remove obstruction. | N.J.A.C. 5:70-3, 1031.1 |  | Unabated | 08/09/2020 | 390 Hackensack Ave,182A
HC | 01/28/2020 | Means of Egress | Each floor of a stairwell shall have a sign indicating a stairwell designation and the floor number (i.e. Stair 1, Floor 2). Have signs posted on each level in each stairwell. | N.J.A.C. 5:70-3, 1031.13 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 03/09/2020 | Means of Egress | Means of egress may not be obstructed, remove obstruction. | N.J.A.C. 5:70-3, 1031.1 |  | Unabated | 04/07/2020 | 21 Shafer Pl
HC | 01/28/2020 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 07/31/2020 | 260 Railroad Ave
HC | 11/14/2019 | Egress Doors | Remove interior door locks. Egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 12/13/2019 | 129 Johnson Ave
HC | 01/29/2020 | Egress Doors | Remove interior door locks. Egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 06/19/2020 | 84 S State St,2nd Flr
HC | 01/29/2020 | Egress Doors | Remove interior door locks. Egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 06/19/2020 | 84 S State St,2nd Flr
HC | 07/23/2019 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 06/03/2020 | 10 First St
HC | 05/07/2020 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 06/05/2020 | 70 Longview Ave
HC | 07/10/2019 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 03/15/2020 | 369 Essex St
HC | 01/28/2020 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 03/19/2020 | 113 Johnson Ave
HC | 06/16/2020 | Egress Doors | Egress doors shall be readily openable from the egress side without the use of a key, special knowledge or effort. | N.J.A.C. 5:70-3, [BE] 1010.1.9 |  | Unabated | 07/15/2020 | 343 S River St
HC | 03/05/2020 | Key Boxes | Knox Box keys need to be updated, contact Fire Prevention to arrange for an appointment to access box and replace keys. 201-646-7685 | N.J.A.C. 5:70-3, 506.2 |  | Unabated | 07/30/2020 | 54 Polifly Rd
HC | 05/26/2020 | Key Boxes | Knox Box keys need to be updated, contact Fire Prevention to arrange for an appointment to access box and replace keys. 201-646-7685 | N.J.A.C. 5:70-3, 506.2 |  | Unabated | 07/28/2020 | 268 Kipp St
HC | 12/11/2019 | Storage | Storage of combustible materials in buildings shall be neat and orderly. Organize area and/or reduce amount of storage. | N.J.A.C. 5:70-3, 315.3 |  | Unabated | 07/30/2020 | 30 Prospect Ave,11
HC | 06/23/2020 | Storage | Storage of materials shall be removed from the area to maintain adequate clearance around equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 03/09/2020 | Storage | Storage of materials shall be removed from the area to maintain adequate clearance around equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 04/07/2020 | 21 Shafer Pl
HC | 02/25/2020 | Storage | Improper Storage, Remove all combustible or flammable storage from in and around stairwells. | N.J.A.C. 5:70-3, 1031.1.1 |  | Unabated | 03/25/2020 | 200 Main St,3
HC | 06/23/2020 | Storage | Storage must be maintained orderly with 24 inch clearance below ceiling (unsprinklered). Remove high storage. | N.J.A.C. 5:70-3, 315.3.1 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 06/23/2020 | Storage | Storage must be maintained orderly with 18 inch clearance below sprinkler head deflector. Remove high storage. | N.J.A.C. 5:70-3, 315.3.1 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 06/16/2020 | Storage | Storage of combustible and/or flammable materials shall be confined to approved storage areas. | N.J.A.C. 5:70-3, 315.3.5 |  | Unabated | 07/15/2020 | 343 S River St
HC | 12/05/2019 | Storage | Storage must be maintained orderly with 18 inch clearance below sprinkler head deflector. Remove high storage. | N.J.A.C. 5:70-3, 315.3.1 |  | Unabated | 07/03/2020 | 140 Hudson St
HC | 03/10/2020 | Storage | Storage of materials shall be removed from the area to maintain adequate clearance around equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 04/08/2020 | 15 Emerald St,A
HC | 03/12/2020 | Storage | Storage of materials shall be removed from the area to maintain adequate clearance around equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 04/10/2020 | 111 Essex St
HC | 02/03/2020 | Storage | Storage of combustible and/or flammable materials shall be confined to approved storage areas. | N.J.A.C. 5:70-3, 315.3.5 |  | Unabated | 03/03/2020 | 483 Main St
HC | 03/03/2020 | Storage | Storage must be maintained orderly with 18 inch clearance below sprinkler head deflector. Remove high storage. | N.J.A.C. 5:70-3, 315.3.1 |  | Unabated | 07/21/2020 | 390 Hackensack Ave,131
HC | 11/18/2019 | Storage | Combustible waste material creating a fire hazard shall not be allowed to accumulate in buildings or structures or upon premises. | N.J.A.C. 5:70-3, 304.1 |  | Unabated | 02/29/2020 | 170 High St
HC | 12/10/2019 | Storage | Combustible waste material creating a fire hazard shall not be allowed to accumulate in buildings or structures or upon premises. | N.J.A.C. 5:70-3, 304.1 |  | Unabated | 01/08/2020 | 26 Anderson St
HC | 12/10/2019 | Storage | Storage of combustible materials in buildings shall be neat and orderly. Organize area and/or reduce amount of storage. | N.J.A.C. 5:70-3, 315.3 |  | Unabated | 01/08/2020 | 26 Anderson St
HC | 10/08/2019 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 11/06/2019 | 184 Main St
HC | 11/13/2019 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 01/06/2020 | 301 Beech St,1ST FL
HC | 10/04/2019 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 12/06/2019 | 853 Main St
HC | 02/13/2020 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 03/13/2020 | 171 Union St
HC | 02/21/2020 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 03/18/2020 | 59 Main St,1
HC | 10/08/2019 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 11/06/2019 | 190 Lodi St,A
HC | 02/21/2020 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 03/21/2020 | 190 Lodi St,A
HC | 04/23/2020 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 07/07/2020 | 235 Main St,Building
HC | 10/08/2019 | Local Fees and LHUs | Failure to pay registration/inspection fee | 88 88-5 |  | Unabated | 11/06/2019 | 219 Main St
HC | 06/23/2020 | Electrical | Clearance required around electrical service equipment (30 in wide x 36 in deep x 78 in height). Remove objects/storage in front of equipment. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 07/22/2020 | 299 Williams Ave
HC | 06/08/2020 | Electrical | Required generators shall be tested at least annually under anticipated loads. Annual transition test shall ensure the transfer time from normal to emergency power is 10 seconds or less. Submit annual report to HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 604.4.1.3 |  | Unabated | 07/07/2020 | 450 Hackensack Ave,1
HC | 03/13/2020 | Electrical | Storage of materials shall be removed from the front of electrical service equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 08/09/2020 | 390 Hackensack Ave,182A
HC | 06/24/2020 | Electrical | Electrical hazards shall be abated. | N.J.A.C. 5:70-3, 605.1 |  | Unabated | 07/23/2020 | 16 Marion St,2
HC | 02/26/2020 | Electrical | Extension cords shall not substitute for permanent wiring, remove cord. | N.J.A.C. 5:70-3, 605.5 |  | Unabated | 03/26/2020 | 139 Main St,BLDG
HC | 02/04/2020 | Electrical | Electrical hazards shall be abated. | N.J.A.C. 5:70-3, 605.1 |  | Unabated | 03/03/2020 | 59 Newman St,2nd Flr
HC | 11/13/2019 | Electrical | Storage of materials shall be removed from the front of electrical service equipment. Clearance shall be 30 inches width, 36 inches depth and 78 inches height. | N.J.A.C. 5:70-3, 605.3 |  | Unabated | 01/28/2020 | 59 Newman St,2nd Flr
HC | 01/09/2020 | Electrical | Electrical hazards shall be abated. | N.J.A.C. 5:70-3, 605.1 |  | Unabated | 02/29/2020 | 24 Bergen St,1st Flr
HC | 02/03/2020 | Electrical | Extension cords shall not substitute for permanent wiring, remove cord. | N.J.A.C. 5:70-3, 605.5 |  | Unabated | 02/29/2020 | 171 S Newman St
HC | 02/03/2020 | Electrical | Multi-plug adapters and unfused plug strips prohibited, remove same. | N.J.A.C. 5:70-3, 605.4 |  | Unabated | 02/29/2020 | 171 S Newman St
HC | 02/03/2020 | Electrical | Electrical hazards shall be abated. | N.J.A.C. 5:70-3, 605.1 |  | Unabated | 02/29/2020 | 171 S Newman St
HC | 02/07/2020 | Electrical | Electrical hazards shall be abated. | N.J.A.C. 5:70-3, 605.1 |  | Unabated | 05/16/2020 | 37 Linden St
HC | 02/05/2020 | Open Flame / Precautions Against Fire | Repair chimney/flu pipe connection. Submit repair report to HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 603.6 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 05/22/2020 | Open Flame / Precautions Against Fire | Outdoor Open Flame Devices i.e. Grills, torches, fireplaces, etc. shall be prohibited on combustible decks or within 5 feet of combustible construction. Exception, electric grills. | N.J.A.C. 5:70-3, 308.1.4 |  | Unabated | 07/30/2020 | 414 Hackensack Ave,1000
HC | 01/28/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 01/28/2020 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 01/28/2020 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 07/30/2020 | 15 First St,Building
HC | 03/04/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 247 Passaic St
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 17 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 17 Cambridge Ter
HC | 03/10/2020 | Multiple Dwelling | Emergency generator annual load test required. Forward report to Fire Prevention HFDFP@Hackensack.org. |  |  | Unabated | 04/08/2020 | 170 Sussex St,Office
HC | 03/09/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 04/07/2020 | 21 Shafer Pl
HC | 09/20/2019 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 09/20/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 10/03/2019 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/27/2020 | 414 Hackensack Ave,2000
HC | 02/06/2020 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 02/06/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 03/06/2020 | 240 Prospect Ave,Building 1
HC | 01/29/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 01/29/2020 | Multiple Dwelling | Emergency generator annual load test required. Forward report to Fire Prevention HFDFP@Hackensack.org. |  |  | Unabated | 07/31/2020 | 380 Prospect Ave
HC | 12/11/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 07/01/2020 | 310 Lookout Ave
HC | 12/11/2019 | Multiple Dwelling | Install or replace missing stairwell reflectors. Green Reflector indicates stairwell leads to a rooftop door, Red indicates stairwell does not. | 88 88-6 |  | Unabated | 07/01/2020 | 310 Lookout Ave
HC | 02/05/2020 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 02/05/2020 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 02/05/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 02/05/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/01/2020 | 15 Lehigh St
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 27 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 27 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 440 Essex St
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 440 Essex St
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 26 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 26 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 445 Thompson St
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 445 Thompson St
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 16 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 16 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 7 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 7 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 2 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 2 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 6 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 6 Cambridge Ter
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 34 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 34 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 20 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 20 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 40 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 40 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 10 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 10 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 07/23/2020 | 30 Arcadia Rd
HC | 02/28/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/23/2020 | 30 Arcadia Rd
HC | 02/26/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 03/26/2020 | 169 Passaic St
HC | 02/20/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 07/03/2020 | 225 Catalpa Ave
HC | 02/25/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 03/25/2020 | 170 Prospect Ave
HC | 02/25/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 03/25/2020 | 170 Prospect Ave
HC | 02/25/2020 | Multiple Dwelling | Wired Carbon Monoxide detectors shall be certified annually. Forward annual report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 06/25/2020 | 173 High St
HC | 02/25/2020 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 06/25/2020 | 173 High St
HC | 09/24/2019 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 05/01/2020 | 265 Beech St
HC | 09/24/2019 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 05/01/2020 | 265 Beech St
HC | 09/24/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 05/01/2020 | 265 Beech St
HC | 09/24/2019 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 05/01/2020 | 275 Beech St
HC | 09/24/2019 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 05/01/2020 | 275 Beech St
HC | 09/24/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 05/01/2020 | 275 Beech St
HC | 09/27/2019 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 09/27/2019 | Multiple Dwelling | Install or replace missing stairwell reflectors. Green Reflector indicates stairwell leads to a rooftop door, Red indicates stairwell does not. | 88 88-6 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 09/27/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 09/27/2019 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 01/28/2020 | 350 Prospect Ave
HC | 10/16/2019 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 01/28/2020 | 100 Second St
HC | 10/16/2019 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 01/28/2020 | 100 Second St
HC | 10/16/2019 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 01/28/2020 | 100 Second St
HC | 10/16/2019 | Multiple Dwelling | Wired unit smoke detectors shall be certified annually by a licensed professional. Forward current report to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 907.8.5 |  | Unabated | 01/28/2020 | 100 Second St
HC | 10/16/2019 | Multiple Dwelling | Current NFPA annual sprinkler and or standpipe report requested. Forward to Fire Prevention HFDFP@Hackensack.org | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 01/28/2020 | 100 Second St
HC | 10/16/2019 | Multiple Dwelling | Provide a copy of NFPA annual Fire Alarm report to Fire Prevention. (201)646-7594 (fax) or HFDFP@Hackensack.org | N.J.A.C. 5:70-3, 907.8 |  | Unabated | 01/28/2020 | 100 Second St
HC | 03/04/2020 | Multiple Dwelling | As of 01/01/2019, all battery operated smoke alarms shall be the 10 year sealed battery type. Replace all battery only detectors. | N.J.A.C. 5:70-4.19.(c) |  | Unabated | 04/02/2020 | 33 Polifly Rd
HC | 03/04/2020 | Multiple Dwelling | Carbon Monoxide detectors shall be maintained. Submit documentation from building representative that all units have a working CO detector within the vicinity of the sleeping areas. HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 901.6.3 |  | Unabated | 04/02/2020 | 33 Polifly Rd
HC | 03/04/2020 | Multiple Dwelling | Submit documentation from a building representative that all unit doors to common areas self close and latch. Forward to Fire Prevention HFDFP@Hackensack.org. | N.J.A.C. 5:70-3, 703.2.3 |  | Unabated | 04/02/2020 | 33 Polifly Rd
HC | 03/04/2020 | Multiple Dwelling | Battery operated smoke alarms shall be maintained, building representative to provide in writing documentation stating detectors are present and are operational. | N.J.A.C. 5:70-3, 907.11.2.2. |  | Unabated | 04/02/2020 | 33 Polifly Rd
HC | 11/12/2019 | Multiple Dwelling | Current NFPA annual sprinkler and or standpipe report requested. Forward to Fire Prevention HFDFP@Hackensack.org | N.J.A.C. 5:70-3, 901.6 |  | Unabated | 06/28/2020 | 100 Prospect Ave